## Sheet1
SunSpec Data Types and NaN Values
The following table shows the data types used in the SunSpec Modbus profile and the possible NaN values. The SunSpec data types are listed in the Type column of the allocation tables. They describe the data width and the format of the data value saved at a register address. The format, such as bit field, describes how SunSpec data is to be interpreted. The formats are important, for example, for the displaying of data or for its further processing:
Type | NaN value [hex] | NaN value [dec] | C data type | Description
acc16 | 0x0000 | 0 | uint16_t | 0 = Not Accumulated.
acc32 | 0x0000 0000 | 0 | uint32_t | Accumulated value (32 bit). Is used for all sequentially increas-ing values.
acc64 | 0x0000 0000 0000 0000 | 0 | uint64_t | Accumulated value (64 bit). Is used for all sequentially increasing values. Only positive values are permitted. The overflow of the number range takes place at 0x7FFF FFFF FFFF FFFF.
bitfield16 | 0xFFFF | 65535 | uint16_t | Bit field (16 bit). A combination of individual bits. Is used for multi-value alarm messages or status. Value range 0 to 0x7FFF. If the MSB is set in a bit field, all other bits are ig-nored.
bitfield32 | 0xFFFF FFFF | 4294967295 | uint32_t | Bit field (32 bit). A combination of individual bits. Is used for multi-value alarm messages or status. Value range 0 to 0x7FFF FFFF. If the MSB is set in a bit field, all other bits are ignored.
enum16 | 0xFFFF | 65535 | uint16_t | Number code (16 bit). The breakdown of the possible codes can be found directly under the designation of the Modbus register in the SunSpec Modbus profile allocation tables.
enum32 | 0xFFFF FFFF | 4294967295 | uint32_t
float32 | 0x7FFF FFFF - 0x7FC0 0000 |  | float32_t | NaN as per IEEE-754.
int16 | 0x8000 | -32768 | int16_t | Signed integer (16 bit).
int32 | 0x8000 0000 | -2147483648 | int32_t | Signed integer (32 bit).
ipaddr32 | 0x0000 | 0 | uint32_t | 0 = Not Configured
string | 0x0000 | 0 | *char | String (multiple of 2 bytes). A zero-terminating value or a value of fixed length.
sunssf | 0x8000 | -32768 | int16_t | SunSpec scale factor as signed integer (16 bit). Scale factors are used as exponents of a power of ten. Negative scale factors push the decimal point to the left, positive scale factors to the right.
uint16 | 0xFFFF | 65535 | uint16_t | Unsigned integer (16 bit).
uint32 | 0xFFFF FFFF | 4294967295 | uint32_t | Unsigned integer (32 bit).
uint64 | 0xFFFF FFFF FFFF FFFF | moc | uint64_t | Unsigned integer (64 bit).