## Index
Model | Label | Description | Notes
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
4 | Secure Dataset Read Response | Compute a digial signature over a specifed set of data registers
5 | Secure Write Request | Include a digial signature along with the control data
6 | Secure Write Sequential Request | Include a digial signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response | Used in conjunction with a Secure Write Request
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
121 | Basic Settings | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
122 | Measurements_Status | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
124 | Storage | Basic Storage Controls | Ref 3: 8.7.4.2
125 | Pricing | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
127 | Freq-Watt Param | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
128 | Dynamic Reactive Current | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
131 | Watt-PF | Watt-Power Factor | Ref 3: 8.11.1.2
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
136 | HFRT | High Frequency Ride-through | Ref 4: 11
137 | LVRTC | LVRT must remain connected | Ref 4: 11
138 | HVRTC | HVRT must remain connected | Ref 4: 11
139 | LVRTX | LVRT extended curve | Ref 4: 11
140 | HVRTX | HVRT extended curve | Ref 4: 11
141 | LFRTC | LFRT must remain connected | Ref 4: 11
142 | HFRTC | HFRT must remain connected | Ref 4: 11
143 | LFRTX | LFRT extended curve | Ref 4: 11
144 | HFRTX | HFRT extended curve | Ref 4: 11
145 | Extended Settings | Inverter controls extended settings
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter |  | Float
212 | split single phase (ABN) meter |  | Float
213 | wye-connect three phase (abcn) meter |  | Float
214 | delta-connect three phase (abc) meter |  | Float
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orienation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorolgical Model | This model supersedes model 301
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner | This model is SUPERSEDED by model 403
402 | String Combiner (Advanced) | An advanced string combiner | This model is SUPERSEDED by model 404
403 | String Combiner (Current) | A basic string combiner model | This model supersedes model 401
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
501 | Solar Module | A solar module model supporing DC-DC converter | Float
502 | Solar Module | A solar module model supporing DC-DC converter | Integer
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller
64400 | Studer Parameter Read / Write | Special Model to read and write Studer-Innotec device parameters
64401 | Studer System Model | Studer-Innotec System Model
64402 | Studer System Phase Value Model | Studer-Innotec System Phase Value Model
64403 | Studer Event Model | Studer-Innotec Event Model
64410 | Studer Xtender Model | Studer-Innotec Xtender Model
64411 | Studer VarioTrack Model | Studer-Innotec VarioTrack Model
64412 | Studer VarioString Model | Studer-Innotec VarioString Model
64413 | Studer BSP Model | Studer-Innotec Battery Status Processor Model

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | All SunSpec compliant devices must include this as the first model
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 2
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Aggregator | 2 | uint16 |  |  | R | M | Aggregates a collection of models for a given model id
Header |  | 1 |  | 1 | L |  | 14 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AID | AID |  | uint16 |  |  | R | M | Aggregated model id
Fixed Block |  | 3 | 1 | 1 | N | N |  | uint16 |  |  | R | M | Number of aggregated models
Fixed Block |  | 4 | 2 | 1 | UN | UN |  | uint16 |  |  | R | M | Update Number. Incrementing nunber each time the mappping is changed. If the number is not changed from thelast reading the direct access to a specific offset will result in reading the same logical model as before. Otherwise the entire model must be read to refresh the changes
Fixed Block |  | 5 | 3 | 1 | St | Status |  | enum16 |  |  | R | M | Enumerated status code
Fixed Block |  | 6 | 4 | 1 | StVnd | Vendor Status |  | enum16 |  |  | R | O | Vendor specific status code
Fixed Block |  | 7 | 5 | 2 | Evt | Event Code |  | bitfield32 |  |  | R | M | Bitmask event code
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event Code |  | bitfield32 |  |  | R | O | Vendor specific event code
Fixed Block |  | 11 | 9 | 1 | Ctl | Control |  | enum16 |  |  | R | O | Control register for all aggregated devices
Fixed Block |  | 12 | 10 | 2 | CtlVnd | Vendor Control |  | enum32 |  |  | R | O | Vendor control register for all aggregated devices
Fixed Block |  | 14 | 12 | 2 | CtlVl | Control Value |  | enum32 |  |  | R | O | Numerical value used as a parameter to the control
enum16 | St |  |  | Name: OFF; Value: 1
enum16 | St |  |  | Name: ON; Value: 2
enum16 | St |  |  | Name: FULL; Value: 3
enum16 | St |  |  | Name: FAULT; Value: 4
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Value: 0
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Value: 1
bitfield32 | Evt |  |  | Name: RESERVED; Value: 11
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Value: 3
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Value: 6
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Value: 7
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Value: 12
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Value: 13
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Value: 14
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Value: 15
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Value: 16
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Value: 17
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Value: 18
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Value: 19
bitfield32 | Evt |  |  | Name: TEST_FAILED; Value: 20
enum16 | Ctl |  |  | Name: NONE; Value: 0
enum16 | Ctl |  |  | Name: AUTOMATIC; Value: 1
enum16 | Ctl |  |  | Name: FORCE_OFF; Value: 2
enum16 | Ctl |  |  | Name: TEST; Value: 3
enum16 | Ctl |  |  | Name: THROTTLE; Value: 4

## 3
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Dataset Read Request | 3 | uint16 |  |  | R | M | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
Header |  | 1 |  | 1 | L |  | 58 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of registers being requested | A max of 50 registers are allowed
Fixed Block |  | 3 | 1 | 1 | Off1 | Offset1 |  | uint16 |  |  | RW | M | Offset of value to read
Fixed Block |  | 4 | 2 | Size: 1; Name: Off2; Type: uint16; R/W: RW | M
Fixed Block |  | 5 | 3 | Size: 1; Name: Off3; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Off4; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Off5; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Off6; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Off7; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Off8; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Off9; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Off10; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Off11; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Off12; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Off13; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Off14; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Off15; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Off16; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Off17; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Off18; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Off19; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Off20; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Off21; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Off22; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Off23; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Off24; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Off25; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Off26; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Off27; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Off28; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Off29; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Off30; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Off31; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Off32; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Off33; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Off34; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Off35; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Off36; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Off37; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Off38; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Off39; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Off40; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Off41; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Off42; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Off43; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Off44; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Off45; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Off46; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Off47; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Off48; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Off49; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Off50; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 55 | 53 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 56 | 54 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 57 | 55 | 1 | Role | Role |  | uint16 |  |  | RW | M | Digital Signature ID | User's role id 0-5
Fixed Block |  | 58 | 56 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 59 | 57 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 60 | 0 | 1 | DS | DS |  | uint16 |  |  | R | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 4
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Dataset Read Response | 4 | uint16 |  |  | R | M | Compute a digial signature over a specifed set of data registers
Header |  | 1 |  | 1 | L |  | 60 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RqSeq | Request Sequence |  | uint16 |  |  | R | M | Sequence number from the request
Fixed Block |  | 3 | 1 | 1 | Sts | Status |  | uint16 |  |  | R | M | Status of last read operation
Fixed Block |  | 4 | 2 | 1 | X | X |  | uint16 |  |  | R | M | Number of values from the request | A max of 50 values are allocated
Fixed Block |  | 5 | 3 | 1 | Val1 | Value1 |  | uint16 |  |  | R | M | Copy of value from register Off1. | Unused values shall return 0xFFFF (unimplemented)
Fixed Block |  | 6 | 4 | Size: 1; Name: Val2; Type: uint16; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Val3; Type: uint16; R/W: R | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val4; Type: uint16; R/W: R | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Val5; Type: uint16; R/W: R | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val6; Type: uint16; R/W: R | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Val7; Type: uint16; R/W: R | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val8; Type: uint16; R/W: R | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Val9; Type: uint16; R/W: R | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val10; Type: uint16; R/W: R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Val11; Type: uint16; R/W: R | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val12; Type: uint16; R/W: R | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Val13; Type: uint16; R/W: R | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val14; Type: uint16; R/W: R | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Val15; Type: uint16; R/W: R | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val16; Type: uint16; R/W: R | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Val17; Type: uint16; R/W: R | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val18; Type: uint16; R/W: R | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Val19; Type: uint16; R/W: R | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val20; Type: uint16; R/W: R | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Val21; Type: uint16; R/W: R | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val22; Type: uint16; R/W: R | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Val23; Type: uint16; R/W: R | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val24; Type: uint16; R/W: R | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Val25; Type: uint16; R/W: R | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val26; Type: uint16; R/W: R | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Val27; Type: uint16; R/W: R | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val28; Type: uint16; R/W: R | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Val29; Type: uint16; R/W: R | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val30; Type: uint16; R/W: R | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Val31; Type: uint16; R/W: R | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val32; Type: uint16; R/W: R | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Val33; Type: uint16; R/W: R | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val34; Type: uint16; R/W: R | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Val35; Type: uint16; R/W: R | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val36; Type: uint16; R/W: R | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Val37; Type: uint16; R/W: R | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val38; Type: uint16; R/W: R | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Val39; Type: uint16; R/W: R | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val40; Type: uint16; R/W: R | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Val41; Type: uint16; R/W: R | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val42; Type: uint16; R/W: R | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Val43; Type: uint16; R/W: R | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val44; Type: uint16; R/W: R | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Val45; Type: uint16; R/W: R | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val46; Type: uint16; R/W: R | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Val47; Type: uint16; R/W: R | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val48; Type: uint16; R/W: R | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Val49; Type: uint16; R/W: R | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val50; Type: uint16; R/W: R | M
Fixed Block |  | 55 | 53 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 57 | 55 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 58 | 56 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of response | Shall be advanced for each reponse
Fixed Block |  | 59 | 57 | 1 | Alm | Alarm |  | enum16 |  |  | R | M | Bitmask alarm code
Fixed Block |  | 60 | 58 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 61 | 59 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 62 | 0 | 1 | DS | DS |  | uint16 |  |  | R | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
uint16 | Sts |  |  | Name: SUCCESS; Label: SUCCESS; Value: 0 |  | Operation succeeded
uint16 | Sts | [11 empty] | Operation failed digital signature check | bar: Name to Value
uint16 | Sts |  |  | Name: ACL; Label: ACL; Value: 2 |  | Operation failed access control check | One or more registers were not writable by this role
uint16 | Sts |  |  | Name: OFF; Label: OFF; Value: 3 |  | Operation failed offset check | Offset out of range or missing from multi-register value
enum16 | Alm |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alm |  |  | Name: ALM; Label: ALARM; Value: 1 |  | Security Alarm | Tampered
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 5
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Request | 5 | uint16 |  |  | R | M | Include a digial signature along with the control data
Header |  | 1 |  | 1 | L |  | 88 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
Fixed Block |  | 3 | 1 | 1 | Off1 | Offset1 |  | uint16 |  |  | RW | M | Offset of control register to write value to
Fixed Block |  | 4 | 2 | 1 | Val1 | Value1 |  | uint16 |  |  | RW | M | Value to write to control register at offset
Fixed Block |  | 5 | 3 | Size: 1; Name: Off2; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Val2; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Off3; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val3; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Off4; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val4; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Off5; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val5; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Off6; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val6; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Off7; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val7; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Off8; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val8; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Off9; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val9; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Off10; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val10; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Off11; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val11; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Off12; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val12; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Off13; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val13; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Off14; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val14; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Off15; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val15; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Off16; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val16; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Off17; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val17; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Off18; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val18; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Off19; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val19; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Off20; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val20; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Off21; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val21; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Off22; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val22; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Off23; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val23; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Off24; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val24; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Off25; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val25; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Off26; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val26; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Off27; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Val27; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Off28; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Val28; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Off29; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Val29; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Off30; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Val30; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Off31; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Val31; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Off32; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Val32; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Off33; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Val33; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Off34; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Val34; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Off35; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Val35; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Off36; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Val36; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Off37; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Val37; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Off38; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Val38; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Off39; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Val39; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Off40; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Val40; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 85 | 83 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 86 | 84 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 87 | 85 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 88 | 86 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 89 | 87 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 90 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 6
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Sequential Request | 6 | uint16 |  |  | R | M | Include a digial signature along with the control data
Header |  | 1 |  | 1 | L |  | 90 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
Fixed Block |  | 3 | 1 | 1 | Off | Offset |  | uint16 |  |  | RW | M | Starting offset for write operation | X values to follow
Fixed Block |  | 4 | 2 | 1 | Val1 | Value1 |  | uint16 |  |  | RW | M | Value to write to control register at offset
Fixed Block |  | 5 | 3 | Size: 1; Name: Val2; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Val3; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Val4; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val5; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Val6; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val7; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Val8; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val9; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Val10; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val11; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Val12; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val13; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Val14; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val15; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Val16; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val17; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Val18; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val19; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Val20; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val21; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Val22; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val23; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Val24; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val25; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Val26; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val27; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Val28; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val29; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Val30; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val31; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Val32; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val33; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Val34; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val35; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Val36; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val37; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Val38; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val39; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Val40; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val41; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Val42; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val43; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Val44; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val45; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Val46; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val47; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Val48; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val49; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Val50; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val51; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Val52; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Val53; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Val54; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Val55; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Val56; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Val57; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Val58; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Val59; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Val60; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Val61; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Val62; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Val63; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Val64; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Val65; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Val66; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Val67; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Val68; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Val69; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Val70; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Val71; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Val72; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Val73; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Val74; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Val75; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Val76; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Val77; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Val78; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Val79; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | Size: 1; Name: Val80; Type: uint16; R/W: RW | M
Fixed Block |  | 84 | 82 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 86 | 84 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 87 | 85 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 88 | 86 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 89 | 87 | Size: 1; Name: Rsrvd; Type: pad; R/W: RW | M
Fixed Block |  | 90 | 88 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 91 | 89 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 92 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 7
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Response Model (DRAFT 1) | 7 | uint16 |  |  | R | M | Include a digital signature over the response | Used in conjunction with a Secure Write Request
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RqSeq | Request Sequence |  | uint16 |  |  | R | M | Sequence number from the request
Fixed Block |  | 3 | 1 | 1 | Sts | Status |  | enum16 |  |  | R | M | Status of last write operation
Fixed Block |  | 4 | 2 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 6 | 4 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 7 | 5 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of response | Shall be advanced for each reponse
Fixed Block |  | 8 | 6 | 1 | Alm | Alarm |  | enum16 |  |  | R | M | Bitmask alarm code
Fixed Block |  | 9 | 7 | Size: 1; Name: Rsrvd; Type: pad; R/W: R | M
Fixed Block |  | 10 | 8 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 11 | 9 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 12 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Sts |  |  | Name: SUCCESS; Label: SUCCESS; Value: 0 |  | Operation succeeded
enum16 | Sts | [11 empty] | Operation failed digital signature check | The signature was not valid | bar: Name to Value
enum16 | Sts |  |  | Name: ACL; Label: ACL; Value: 2 |  | Operation failed access control check | One or more registers were not writable by this role
enum16 | Sts |  |  | Name: OFF; Label: OFF; Value: 3 |  | Operation failed offset check | Offset out of range or missing from multi-register value
enum16 | Sts |  |  | Name: VAL; Label: VAL; Value: 4 |  | Operation failed valid value check | Value is out of acceptable range
enum16 | Alm |  |  | Name: NONE; Label: NONE; Value: 0 |  | No Alarms
enum16 | Alm |  |  | Name: ALM; Label: ALARM; Value: 1 |  | Security Alarm | Tampered
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No Alarms
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 8
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Get Device Security Certificate | 8 | uint16 |  |  | R | M | Security model for PKI
Header |  | 1 |  | 1 | L |  | 2 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Fmt | Format |  | enum16 |  |  | R | M | X.509 format of the certificate. DER or PEM.
Fixed Block |  | 3 | 1 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers to follow for the certificate
Repeating Block |  | 4 | 0 | 1 | Cert | Cert |  | uint16 |  |  | R | M | X.509 Certificate of the device
enum16 | Fmt |  |  | Name: NONE; Label: NONE; Value: 0
enum16 | Fmt |  |  | Name: X509_PEM; Label: PEM; Value: 1
enum16 | Fmt |  |  | Name: X509_DER; Label: DER; Value: 2

## 9
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Set Operator Security Certificate | 9 | uint16 |  |  | R | M | Security model for PKI
Header |  | 1 |  | 1 | L |  | 92 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | CertUID | Cert_UID |  | uint16 |  |  | RW | M | User ID for this certificate
Fixed Block |  | 3 | 1 | 1 | CertRole | Cert_Role |  | uint16 |  |  | RW | M | Role for this certificate
Fixed Block |  | 4 | 2 | 1 | Fmt | Format |  | enum16 |  |  | RW | M | Format of this certificate
Fixed Block |  | 5 | 3 | 1 | Typ | Type |  | enum16 |  |  | RW | M | Type of this certificate
Fixed Block |  | 6 | 4 | 1 | TotLn | Total Length |  | uint16 |  |  | RW | M | Total Length of the Certificate | In registers, zero padded.
Fixed Block |  | 7 | 5 | 1 | FrgLn | Fragment length |  | uint16 |  |  | RW | M | Length of this fragment | Maximum fragment length is 80 registers
Fixed Block |  | 8 | 6 | 1 | Frg1 | Frag1 |  | uint16 |  |  | RW | M | First word of this fragment
Fixed Block |  | 9 | 7 | Size: 1; Name: Frg2; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Frg3; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Frg4; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Frg5; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Frg6; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Frg7; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Frg8; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Frg9; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Frg10; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Frg11; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Frg12; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Frg13; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Frg14; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Frg15; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Frg16; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Frg17; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Frg18; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Frg19; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Frg20; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Frg21; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Frg22; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Frg23; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Frg24; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Frg25; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Frg26; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Frg27; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Frg28; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Frg29; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Frg30; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Frg31; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Frg32; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Frg33; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Frg34; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Frg35; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Frg36; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Frg37; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Frg38; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Frg39; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Frg40; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Frg41; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Frg42; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Frg43; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Frg44; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Frg45; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Frg46; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Frg47; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Frg48; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Frg49; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Frg50; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Frg51; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Frg52; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Frg53; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Frg54; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Frg55; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Frg56; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Frg57; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Frg58; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Frg59; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Frg60; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Frg61; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Frg62; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Frg63; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Frg64; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Frg65; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Frg66; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Frg67; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Frg68; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Frg69; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Frg70; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Frg71; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Frg72; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Frg73; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Frg74; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Frg75; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | Size: 1; Name: Frg78; Type: uint16; R/W: RW | M
Fixed Block |  | 84 | 82 | Size: 1; Name: Frg79; Type: uint16; R/W: RW | M
Fixed Block |  | 85 | 83 | 1 | Frg80 | Frag80 |  | uint16 |  |  | RW | M | Last word of this fragment
Fixed Block |  | 86 | 84 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 88 | 86 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 89 | 87 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 90 | 88 | 1 | UID | UID |  | uint16 |  |  | RW | M | User ID for the request signature
Fixed Block |  | 91 | 89 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 92 | 90 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 93 | 91 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers to follow for the certificate
Repeating Block |  | 94 | 0 | Size: 1; Name: Cert; Type: uint16; R/W: RW | M
enum16 | Fmt |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Fmt |  |  | Name: X509_PEM; Label: PEM; Value: 1
enum16 | Fmt |  |  | Name: X509_DER; Label: DER; Value: 2
enum16 | Typ |  |  | Name: DEV_KEY_PAIR; Value: 0
enum16 | Typ |  |  | Name: DEV_SHARED_KEY; Value: 1
enum16 | Typ |  |  | Name: OPERATOR_PUB; Value: 2
enum16 | Typ |  |  | Name: OPERATOR_SHARED; Value: 3
enum16 | Typ |  |  | Name: CA_PUB; Value: 4
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 10
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Communication Interface Header | 10 | uint16 |  |  | R | M | To be included first for a complete interface description
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | St | Interface Status |  | enum16 |  |  | R | M | Overall interface status
Fixed Block |  | 3 | 1 | 1 | Ctl | Interface Control |  | uint16 |  |  | RW | O | Overall interface control (TBD)
Fixed Block |  | 4 | 2 | 1 | Typ | Physical Access Type |  | enum16 |  |  | R | O | Enumerated value. Type of physical media
Fixed Block |  | 5 | 3 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | St |  |  | Name: DOWN; Label: down; Value: 0 |  | Interface is down
enum16 | St |  |  | Name: UP; Label: up; Value: 1 |  | Interface is up
enum16 | St |  |  | Name: FAULT; Label: fault; Value: 2 |  | Interface is in a fault state
enum16 | Typ |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unkown media
enum16 | Typ |  |  | Name: INTERNAL; Label: internal; Value: 1 |  | Internal e.g. embbedded switch
enum16 | Typ |  |  | Name: TWISTED_PAIR; Label: twisted pair; Value: 2 |  | Twisted Pair
enum16 | Typ |  |  | Name: FIBER; Label: fiber; Value: 3 |  | Fiber
enum16 | Typ |  |  | Name: WIRELESS; Value: 4
enum16 | Typ |  |  | Label: wifi; Value: 4 |  | WIFI

## 11
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Ethernet Link Layer | 11 | uint16 |  |  | R | M | Include to support a wired ethernet port
Header |  | 1 |  | 1 | L |  | 13 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Spd | Ethernet Link Speed |  | uint16 | Mbps |  | R | M | Interface speed in Mb/s
Fixed Block |  | 3 | 1 | 1 | CfgSt | Interface Status Flags |  | bitfield16 |  |  | R | M | Bitmask values Interface flags.
Fixed Block |  | 4 | 2 | 1 | St | Link State |  | enum16 |  |  | R | M | Enumerated value. State information for this interface
Fixed Block |  | 5 | 3 | 4 | MAC | MAC |  | eui48 |  |  | R | O | IEEE MAC address of this interface
Fixed Block |  | 9 | 7 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 13 | 11 | 1 | Ctl | Control |  | bitfield16 |  |  | RW | O | Control flags
Fixed Block |  | 14 | 12 | 1 | FrcSpd | Forced Speed |  | uint16 | Mbps |  | RW | O | Forced interface speed in Mb/s when AUTO is disabled
bitfield16 | CfgSt |  |  | Name: LINK; Label: link status; Value: 0 |  | link is up
bitfield16 | CfgSt |  |  | Name: FULL_DUPLEX; Label: duplex; Value: 1 |  | Force full duplex
bitfield16 | CfgSt |  |  | Name: AUTO_NEG1; Label: auto negotiation 1; Value: 2 |  | Auto-negotiation bits are encoded as: 000 - inprogress. 001 - speed detection has failed. 010 - negotiation has failed. 011 - negotiated speed and duplex. 100 - negotiation not attempted.
bitfield16 | CfgSt |  |  | Name: AUTO_NEG2; Label: auto negotiation 2; Value: 3 |  | See AUTO_NEG1
bitfield16 | CfgSt |  |  | Name: AUTO_NEG3; Label: auto negotiation 3; Value: 4 |  | See AUTO_NEG1
bitfield16 | CfgSt |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 5 |  | Setting requires reset
bitfield16 | CfgSt |  |  | Name: HW_FAULT; Label: hw fault; Value: 6 |  | Hardware fault
enum16 | St |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown state
enum16 | St |  |  | Name: ENABLED; Label: enabled; Value: 1 |  | Link is enabled and read
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 2 |  | Link is disabled
enum16 | St |  |  | Name: TESTING; Label: testing; Value: 3 |  | Link is in test
bitfield16 | Ctl |  |  | Name: AUTO; Label: auto; Value: 0 |  | Enable auto-negotiatition
bitfield16 | Ctl |  |  | Name: FULL_DUPLEX; Label: duplex; Value: 1 |  | Force full duplex

## 12
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | IPv4 | 12 | uint16 |  |  | R | M | Include to support an IPv4 protocol stack on this interface
Header |  | 1 |  | 1 | L |  | 98 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 1 | CfgSt | Config Status |  | enum16 |  |  | R | M | Enumerated value. Configuration status
Fixed Block |  | 7 | 5 | 1 | ChgSt | Change Status |  | bitfield16 |  |  | R | M | Bitmask value. A configuration change is pending
Fixed Block |  | 8 | 6 | 1 | Cap | Config Capability |  | bitfield16 |  |  | R | M | Bitmask value. Identify capable sources of configuration
Fixed Block |  | 9 | 7 | 1 | Cfg | IPv4 Config |  | enum16 |  |  | RW | M | Enumerated value. Configuration method used.
Fixed Block |  | 10 | 8 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Configure use of services
Fixed Block |  | 11 | 9 | 8 | Addr | IP |  | string |  |  | RW | M | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 19 | 17 | 8 | Msk | Netmask |  | string |  |  | RW | M | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 27 | 25 | 8 | Gw | Gateway |  | string |  |  | RW | O | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 35 | 33 | 8 | DNS1 | DNS1 |  | string |  |  | RW | O | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 43 | 41 | 8 | DNS2 | DNS2 |  | string |  |  | RW | O | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 51 | 49 | 12 | NTP1 | NTP1 |  | string |  |  | RW | O | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 63 | 61 | 12 | NTP2 | NTP2 |  | string |  |  | RW | O | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 75 | 73 | 12 | DomNam | Domain |  | string |  |  | RW | O | Domain name (24 chars max)
Fixed Block |  | 87 | 85 | 12 | HostNam | Host Name |  | string |  |  | RW | O | Host name (24 chars max)
Fixed Block |  | 99 | 97 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | CfgSt |  |  | Name: NOT_CONFIGURED; Label: not configured; Value: 0 |  | the stack is not configured
enum16 | CfgSt |  |  | Name: VALID_SETTING; Label: valid setting; Value: 1 |  | a valid configuration from BOOTP, DHCP, or NV mem
enum16 | CfgSt |  |  | Name: VALID_HW; Label: valid hardware; Value: 2 |  | a valid configuration from hardware settings
bitfield16 | ChgSt |  |  | Name: PENDING; Label: pending; Value: 0 |  | a configuration change is pending
bitfield16 | Cap |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
bitfield16 | Cap |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
bitfield16 | Cap |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
bitfield16 | Cap |  |  | Name: DNS; Label: DNS; Value: 3 |  | DNS Client capable
bitfield16 | Cap |  |  | Name: CFG_SETTABLE; Label: configurable; Value: 4 |  | Settable configuration capable
bitfield16 | Cap |  |  | Name: HW_CONFIG; Label: hw; Value: 5 |  | Hardware configuration capable
bitfield16 | Cap |  |  | Name: NTP_CLIENT; Label: ntp; Value: 6 |  | NTP Client capable
bitfield16 | Cap |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 7 |  | configuration change requires reset
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | Use static IP
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
enum16 | Cfg |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
enum16 | Cfg |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP

## 13
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | IPv6 | 13 | uint16 |  |  | R | M | Include to support an IPv6 protocol stack on this interface
Header |  | 1 |  | 1 | L |  | 174 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 1 | CfgSt | Config Status |  | enum16 |  |  | R | M | Enumerated value. Configuration status
Fixed Block |  | 7 | 5 | 1 | ChgSt | Change Status |  | bitfield16 |  |  | R | M | Bitmask value. A configuration change is pending
Fixed Block |  | 8 | 6 | 1 | Cap | Config Capability |  | bitfield16 |  |  | R | M | Bitmask value. Identify capable sources of configuration
Fixed Block |  | 9 | 7 | 1 | Cfg | IPv6 Config |  | enum16 |  |  | RW | M | Enumerated value. Configuration method used.
Fixed Block |  | 10 | 8 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Bitmask value. Configure use of services
Fixed Block |  | 11 | 9 | 20 | Addr | IP |  | string |  |  | RW | M | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 31 | 29 | 20 | CIDR | CIDR |  | string |  |  | RW | O | Classless Inter-Domain Routing Number
Fixed Block |  | 51 | 49 | 20 | Gw | Gateway |  | string |  |  | RW | O | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 71 | 69 | 20 | DNS1 | DNS1 |  | string |  |  | RW | O | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 91 | 89 | 20 | DNS2 | DNS2 |  | string |  |  | RW | O | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 111 | 109 | 20 | NTP1 | NTP1 |  | string |  |  | RW | O | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 131 | 129 | 20 | NTP2 | NTP2 |  | string |  |  | RW | O | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 151 | 149 | 12 | DomNam | Domain |  | string |  |  | RW | O | Domain name (24 chars max)
Fixed Block |  | 163 | 161 | 12 | HostNam | Host Name |  | string |  |  | RW | O | Host name (24 chars max)
Fixed Block |  | 175 | 173 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | CfgSt |  |  | Name: NOT_CONFIGURED; Label: not configured; Value: 0 |  | the stack is not configured
enum16 | CfgSt |  |  | Name: VALID_SETTING; Label: valid setting; Value: 1 |  | a valid configuration from BOOTP, DHCP, or NV mem
enum16 | CfgSt |  |  | Name: VALID_HW; Label: valid hardware; Value: 2 |  | a valid configuration from hardware settings
bitfield16 | ChgSt |  |  | Name: PENDING; Label: pending; Value: 0 |  | a configuration change is pending
bitfield16 | Cap |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
bitfield16 | Cap |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
bitfield16 | Cap |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
bitfield16 | Cap |  |  | Name: DNS; Label: DNS; Value: 3 |  | DNS Client capable
bitfield16 | Cap |  |  | Name: CFG_SETTABLE; Label: configurable; Value: 4 |  | Settable configuration capable
bitfield16 | Cap |  |  | Name: HW_CONFIG; Label: hw; Value: 5 |  | Hardware configuration capable
bitfield16 | Cap |  |  | Name: NTP_CLIENT; Label: ntp; Value: 6 |  | NTP Client capable
bitfield16 | Cap |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 7 |  | configuration change requires reset
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | Use static IP
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
enum16 | Cfg |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
enum16 | Cfg |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP

## 14
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Proxy Server | 14 | uint16 |  |  | R | M | Include this block to allow for a proxy server
Header |  | 1 |  | 1 | L |  | 52 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 6 | 4 | 1 | Cap | Capabilities |  | bitfield16 |  |  | RW | M | Bitmask value. Proxy configuration capabilites
Fixed Block |  | 7 | 5 | 1 | Cfg | Config |  | enum16 |  |  | RW | M | Enumerated value. Set proxy address type
Fixed Block |  | 8 | 6 | 1 | Typ | Type |  | bitfield16 |  |  | RW | M | Enumerate value. Proxy server type
Fixed Block |  | 9 | 7 | 20 | Addr | Address |  | string |  |  | RW | M | IPv4 or IPv6 proxy hostname or dotteed address (40 chars)
Fixed Block |  | 29 | 27 | 1 | Port | Port |  | uint16 |  |  | RW | M | Proxy port number
Fixed Block |  | 30 | 28 | 12 | User | Username |  | string |  |  | RW | O | Proxy user name
Fixed Block |  | 42 | 40 | 12 | Pw | Password |  | string |  |  | RW | O | Proxy password
bitfield16 | Cap |  |  | Name: NO_PROXY; Label: No Proxy; Value: 0 |  | Turn off the proxy
bitfield16 | Cap |  |  | Name: IPV4_PROXY; Label: IPv4 Proxy; Value: 1 |  | Can proxy IPv4
bitfield16 | Cap |  |  | Name: IPV6_PROXY; Label: IPv6 Proxy; Value: 2 |  | Can proxy IPv6

## 15
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Interface Counters Model | 15 | uint16 |  |  | R | M | Interface counters
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Clr | Clear |  | uint16 |  |  | RW | O | Write a "1" to clear all counters
Fixed Block |  | 3 | 1 | 2 | InCnt | Input Count |  | acc32 |  |  | R | O | Number of bytes received
Fixed Block |  | 5 | 3 | 2 | InUcCnt | Input Unicast Count |  | acc32 |  |  | R | O | Number of Unicast packets received
Fixed Block |  | 7 | 5 | 2 | InNUcCnt | Input Non-Unicast Count |  | acc32 |  |  | R | O | Number of non-Unicast packets received
Fixed Block |  | 9 | 7 | 2 | InDscCnt | Input Discarded Count |  | acc32 |  |  | R | O | Number of inbound packets received on the interface but discarded
Fixed Block |  | 11 | 9 | 2 | InErrCnt | Input Error Count |  | acc32 |  |  | R | O | Number of inbound packets that contain errors (excluding discards)
Fixed Block |  | 13 | 11 | 2 | InUnkCnt | Input Unknown Count |  | acc32 |  |  | R | O | Number of inbound packets with unknown protocol
Fixed Block |  | 15 | 13 | 2 | OutCnt | Output Count |  | acc32 |  |  | R | O | Total number of bytes transmitted on this interface
Fixed Block |  | 17 | 15 | 2 | OutUcCnt | Output Unicast Count |  | acc32 |  |  | R | O | Number of Unicast packets transmitted
Fixed Block |  | 19 | 17 | 2 | OutNUcCnt | Output Non-Unicast Count |  | acc32 |  |  | R | O | Number of Non-Unicast packets transmitted
Fixed Block |  | 21 | 19 | 2 | OutDscCnt | Output Discarded Count |  | acc32 |  |  | R | O | Number of Discarded output packets
Fixed Block |  | 23 | 21 | 2 | OutErrCnt | Output Error Count |  | acc32 |  |  | R | O | Number of outbound error packets
Fixed Block |  | 25 | 23 | Size: 1; Name: Pad; Type: pad; R/W: R | O

## 16
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Simple IP Network | 16 | uint16 |  |  | R | M | Include this model for a simple IPv4 network stack
Header |  | 1 |  | 1 | L |  | 52 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name. (8 chars)
Fixed Block |  | 6 | 4 | 1 | Cfg | Config |  | enum16 |  |  | R | M | Enumerated value. Force IPv4 configuration method
Fixed Block |  | 7 | 5 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Bitmask value Configure use of services
Fixed Block |  | 8 | 6 | 8 | Addr | Address |  | string |  |  | RW | M | IP addreess
Fixed Block |  | 16 | 14 | 8 | Msk | Netmask |  | string |  |  | RW | M | Netmask
Fixed Block |  | 24 | 22 | 8 | Gw | Gateway |  | string |  |  | RW | O | Gateway IP address
Fixed Block |  | 32 | 30 | 8 | DNS1 | DNS1 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 40 | 38 | 8 | DNS2 | DNS2 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 48 | 46 | 4 | MAC | MAC |  | uint64 |  |  | R | O | IEEE MAC address of this interface
Fixed Block |  | 52 | 50 | 1 | LnkCtl | Link Control |  | bitfield16 |  |  | RW | O | Bitmask value. Link control flags
Fixed Block |  | 53 | 51 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | A static IP address is assigned
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP to acquire an IP address
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS use
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP use
bitfield16 | LnkCtl |  |  | Name: AUTONEGOTIATE; Label: auto-negotiate; Value: 0 |  | Enable auto-negotiation
bitfield16 | LnkCtl |  |  | Name: FULL_DUPLEX; Label: full duplex; Value: 1 |  | Force full duplex operation
bitfield16 | LnkCtl |  |  | Name: FORCE_10MB; Label: 10Mbs; Value: 2 |  | Force 10 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_100MB; Label: 100Mbs; Value: 3 |  | Force 100 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_1GB; Label: 1Gbs; Value: 3 |  | Force 1 Gb/s link speed

## 17
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Serial Interface | 17 | uint16 |  |  | R | M | Include this model for serial interface configuration support
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 6 | 4 | 2 | Rte | Rate |  | uint32 | bps |  | RW | M | Interface baud rate in bits per second
Fixed Block |  | 8 | 6 | 1 | Bits | Bits |  | uint16 |  |  | RW | M | Number of data bits per character
Fixed Block |  | 9 | 7 | 1 | Pty | Parity |  | enum16 |  |  | RW | M | Bitmask value. Parity setting
Fixed Block |  | 10 | 8 | 1 | Dup | Duplex |  | enum16 |  |  | RW | O | Enumerated value. Duplex mode
Fixed Block |  | 11 | 9 | 1 | Flw | Flow Control |  | enum16 |  |  | RW | O | Flow Control Method
Fixed Block |  | 12 | 10 | 1 | Typ | Interface Type |  | enum16 |  |  | R | O | Enumerated value. Interface type
Fixed Block |  | 13 | 11 | 1 | Pcol | Protocol |  | enum16 |  |  | R | O | Enumerated value. Serial protocol selection
enum16 | Pty |  |  | Name: NONE; Label: none; Value: 0 |  | No flow control
enum16 | Pty |  |  | Name: ODD; Label: odd; Value: 1 |  | Odd Parity
enum16 | Pty |  |  | Name: EVEN; Label: even; Value: 2 |  | Even Parity
enum16 | Dup |  |  | Name: FULL; Label: full; Value: 0 |  | Full Duplex
enum16 | Dup |  |  | Name: HALF; Label: half; Value: 1 |  | Half Duplex
enum16 | Flw |  |  | Name: NONE; Label: none; Value: 0 |  | No flow control
enum16 | Flw |  |  | Name: HW; Label: hardware; Value: 1 |  | Hardware flow control
enum16 | Flw |  |  | Name: XONXOFF; Label: software; Value: 2 |  | Soft (XON/XOFF) flow control
enum16 | Typ |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown protocol
enum16 | Typ |  |  | Name: RS232; Label: RS232; Value: 1 |  | RS232 interface type
enum16 | Typ |  |  | Name: RS485; Label: RS485; Value: 2 |  | RS485 interface type
enum16 | Pcol |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown protocol
enum16 | Pcol |  |  | Name: MODBUS; Label: Modbus; Value: 1 |  | Modbus protocol
enum16 | Pcol |  |  | Name: VENDOR; Label: vendor specific; Value: 2

## 18
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Cellular Link | 18 | uint16 |  |  | R | M | Include this model to support a cellular interface link
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 2 | IMEI | IMEI |  | uint32 |  |  | RW | O | International Mobile Equipment Identifier for the interface
Fixed Block |  | 8 | 6 | 4 | APN | APN |  | string |  |  | RW | O | Access Point Name for the interface
Fixed Block |  | 12 | 10 | 6 | Num | Number |  | string |  |  | RW | O | Phone number for the interface
Fixed Block |  | 18 | 16 | 6 | Pin | PIN |  | string |  |  | RW | O | Personal Identification Number for the interface

## 19
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | PPP Link | 19 | uint16 |  |  | R | M | Include this model to configure a Point-to-Point Protocol link
Header |  | 1 |  | 1 | L |  | 30 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 2 | Rte | Rate |  | uint32 | bps |  | RW | M | Interface baud rate in bits per second
Fixed Block |  | 8 | 6 | 1 | Bits | Bits |  | uint16 |  |  | RW | M | Number of data bits per character
Fixed Block |  | 9 | 7 | 1 | Pty | Parity |  | enum16 |  |  | RW | M | Bitmask value. Parity setting
Fixed Block |  | 10 | 8 | 1 | Dup | Duplex |  | enum16 |  |  | RW | O | Enumerated value. Duplex mode
Fixed Block |  | 11 | 9 | 1 | Flw | Flow Control |  | enum16 |  |  | RW | O | Flow Control Method
Fixed Block |  | 12 | 10 | 1 | Auth | Authentication |  | enum16 |  |  | R | O | Enumerated value. Authentication method
Fixed Block |  | 13 | 11 | 12 | UsrNam | Username |  | string |  |  | R | O | Username for authentication
Fixed Block |  | 25 | 23 | 6 | Pw | Password |  | string |  |  | R | O | Password for authentication
Fixed Block |  | 31 | 29 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | Pty |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Pty |  |  | Name: ODD; Label: odd; Value: 1 |  | Odd Parity
enum16 | Pty |  |  | Name: EVEN; Label: even; Value: 2 |  | Even Parity
enum16 | Dup |  |  | Name: FULL; Label: full; Value: 0 |  | Full Duplex
enum16 | Dup |  |  | Name: HALF; Label: half; Value: 1 |  | Half Duplex
enum16 | Flw |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Flw |  |  | Name: HW; Label: hardware; Value: 1 |  | Hardware flow control
enum16 | Flw |  |  | Name: XONXOFF; Label: software; Value: 2 |  | Soft (XON/XOFF) flow control
enum16 | Auth |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Auth |  |  | Name: PAP; Label: PAP; Value: 1 |  | Use PAP authentication
enum16 | Auth |  |  | Name: CHAP; Label: CHAP; Value: 2 |  | Use CHAP authentication

## 101
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Single Phase) | 101 | uint16 |  |  | R | M | Include this model for single phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | O | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid disconnect; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 102
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Split-Phase) | 102 | uint16 |  |  | R | M | Include this model for split phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 103
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Three Phase) | 103 | uint16 |  |  | R | M | Include this model for three phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | M | Phase C Current | Connected Phase
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | M | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 111
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Single Phase) FLOAT | 111 | uint16 |  |  | R | M | Include this model for single phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | O | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: ggOFF; Value: 1
enum16 | St |  |  | Name: ggSLEEPING; Value: 2
enum16 | St |  |  | Name: ggSTARTING; Value: 3
enum16 | St |  |  | Name: ggMPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: ggTHROTTLED; Value: 5
enum16 | St |  |  | Name: ggSHUTTING_DOWN; Value: 6
enum16 | St |  |  | Name: ggFAULT; Value: 7
enum16 | St |  |  | Name: ggSTANDBY; Value: 8
enum16 | St |  |  | Label: Off; Value: 8 |  | Device is not operating
enum16 | St |  |  | Label: Sleeping; Value: 8 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Label: Starting; Value: 8 |  | Device is staring up
enum16 | St |  |  | Label: Throttled; Value: 8 |  | Device is operating at reduced power output
enum16 | St |  |  | Label: Shutting down; Value: 8 |  | Device is shutting down
enum16 | St |  |  | Label: Fault; Value: 8 |  | One or more faults exist
enum16 | St |  |  | Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 112
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Split Phase) FLOAT | 112 | uint16 |  |  | R | M | Include this model for split phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current | Connected Phase
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 113
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Three Phase) FLOAT | 113 | uint16 |  |  | R | M | Include this model for three phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current | Sum of active phases
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current | Connected Phase
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current | Connected Phase
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | M | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 120
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Nameplate | 120 | uint16 |  |  | R | M | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 26 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DERTyp | DERTyp |  | enum16 |  |  | R | M | Type of DER device. Default value is 4 to indicate PV device.
Fixed Block |  | 3 | 1 | 1 | WRtg | WRtg |  | uint16 | W | WRtg_SF | R | M | Continuous power output capability of the inverter.
Fixed Block |  | 4 | 2 | 1 | WRtg_SF | WRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 5 | 3 | 1 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | R | M | Continuous Volt-Ampere capability of the inverter.
Fixed Block |  | 6 | 4 | 1 | VARtg_SF | VARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 7 | 5 | 1 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 1.
Fixed Block |  | 8 | 6 | 1 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 2.
Fixed Block |  | 9 | 7 | 1 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 3.
Fixed Block |  | 10 | 8 | 1 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 4.
Fixed Block |  | 11 | 9 | 1 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 12 | 10 | 1 | ARtg | ARtg |  | uint16 | A | ARtg_SF | R | M | Maximum RMS AC current level capability of the inverter. | Sum of all connected phases. Current rating under nominal voltage under nominal power factor.
Fixed Block |  | 13 | 11 | 1 | ARtg_SF | ARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 14 | 12 | 1 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 1. | EEI sign convention.
Fixed Block |  | 15 | 13 | 1 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 2. | EEI sign convention.
Fixed Block |  | 16 | 14 | 1 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 3. | EEI sign convention.
Fixed Block |  | 17 | 15 | 1 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 4. | EEI sign convention.
Fixed Block |  | 18 | 16 | 1 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 19 | 17 | 1 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | R | O | Nominal energy rating of storage device.
Fixed Block |  | 20 | 18 | 1 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 21 | 19 | 1 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | R | O | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
Fixed Block |  | 22 | 20 | 1 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | R | O | Scale factor for amp-hour rating.
Fixed Block |  | 23 | 21 | 1 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | R | O | Maximum rate of energy transfer into the storage device.
Fixed Block |  | 24 | 22 | 1 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 25 | 23 | 1 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | R | O | Maximum rate of energy transfer out of the storage device.
Fixed Block |  | 26 | 24 | 1 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 27 | 25 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
enum16 | DERTyp |  |  | Name: PV; Value: 4
enum16 | DERTyp |  |  | Name: PV_STOR; Value: 82

## 121
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Settings | 121 | uint16 |  |  | R | M | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 30 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WMax | WMax |  | uint16 | W | WMax_SF | RW | M | Setting for maximum power output. Default to WRtg.
Fixed Block |  | 3 | 1 | 1 | VRef | VRef |  | uint16 | V | VRef_SF | RW | M | Voltage at the PCC.
Fixed Block |  | 4 | 2 | 1 | VRefOfs | VRefOfs |  | int16 | V | VRefOfs_SF | RW | M | Offset from PCC to inverter.
Fixed Block |  | 5 | 3 | 1 | VMax | VMax |  | uint16 | V | VMinMax_SF | RW | O | Setpoint for maximum voltage.
Fixed Block |  | 6 | 4 | 1 | VMin | VMin |  | uint16 | V | VMinMax_SF | RW | O | Setpoint for minimum voltage.
Fixed Block |  | 7 | 5 | 1 | VAMax | VAMax |  | uint16 | VA | VAMax_SF | RW | O | Setpoint for maximum apparent power. Default to VARtg.
Fixed Block |  | 8 | 6 | 1 | VArMaxQ1 | VArMaxQ1 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1.
Fixed Block |  | 9 | 7 | 1 | VArMaxQ2 | VArMaxQ2 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
Fixed Block |  | 10 | 8 | 1 | VArMaxQ3 | VArMaxQ3 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
Fixed Block |  | 11 | 9 | 1 | VArMaxQ4 | VArMaxQ4 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
Fixed Block |  | 12 | 10 | 1 | WGra | WGra |  | uint16 | % WMax/sec | WGra_SF | RW | O | Default ramp rate of change of active power due to command or internal action.
Fixed Block |  | 13 | 11 | 1 | PFMinQ1 | PFMinQ1 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | EEI sign convention.
Fixed Block |  | 14 | 12 | 1 | PFMinQ2 | PFMinQ2 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | EEI sign convention.
Fixed Block |  | 15 | 13 | 1 | PFMinQ3 | PFMinQ3 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | EEI sign convention.
Fixed Block |  | 16 | 14 | 1 | PFMinQ4 | PFMinQ4 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | EEI sign convention.
Fixed Block |  | 17 | 15 | 1 | VArAct | VArAct |  | enum16 |  |  | RW | O | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
Fixed Block |  | 18 | 16 | 1 | ClcTotVA | ClcTotVA |  | enum16 |  |  | RW | O | Calculation method for total apparent power. 1=vector 2=arithmetic.
Fixed Block |  | 19 | 17 | 1 | MaxRmpRte | MaxRmpRte |  | uint16 | % WGra | MaxRmpRte_SF | RW | O | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
Fixed Block |  | 20 | 18 | 1 | ECPNomHz | ECPNomHz |  | uint16 | Hz | ECPNomHz_SF | RW | O | Setpoint for nominal frequency at the ECP.
Fixed Block |  | 21 | 19 | 1 | ConnPh | ConnPh |  | enum16 |  |  | RW | O | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
Fixed Block |  | 22 | 20 | 1 | WMax_SF | WMax_SF |  | sunssf |  |  | R | M | Scale factor for real power.
Fixed Block |  | 23 | 21 | 1 | VRef_SF | VRef_SF |  | sunssf |  |  | R | M | Scale factor for voltage at the PCC.
Fixed Block |  | 24 | 22 | 1 | VRefOfs_SF | VRefOfs_SF |  | sunssf |  |  | R | M | Scale factor for offset voltage.
Fixed Block |  | 25 | 23 | 1 | VMinMax_SF | VMinMax_SF |  | sunssf |  |  | R | O | Scale factor for min/max voltages.
Fixed Block |  | 26 | 24 | 1 | VAMax_SF | VAMax_SF |  | sunssf |  |  | R | O | Scale factor for apparent power.
Fixed Block |  | 27 | 25 | 1 | VArMax_SF | VArMax_SF |  | sunssf |  |  | R | O | Scale factor for reactive power.
Fixed Block |  | 28 | 26 | 1 | WGra_SF | WGra_SF |  | sunssf |  |  | R | O | Scale factor for default ramp rate.
Fixed Block |  | 29 | 27 | 1 | PFMin_SF | PFMin_SF |  | sunssf |  |  | R | O | Scale factor for minimum power factor.
Fixed Block |  | 30 | 28 | 1 | MaxRmpRte_SF | MaxRmpRte_SF |  | sunssf |  |  | R | O | Scale factor for maximum ramp percentage.
Fixed Block |  | 31 | 29 | 1 | ECPNomHz_SF | ECPNomHz_SF |  | sunssf |  |  | R | O | Scale factor for nominal frequency.
enum16 | VArAct |  |  | Name: SWITCH; Value: 1
enum16 | VArAct |  |  | Name: MAINTAIN; Value: 2
enum16 | ClcTotVA |  |  | Name: VECTOR; Value: 1
enum16 | ClcTotVA |  |  | Name: ARITHMETIC; Value: 2
enum16 | ConnPh | bar: Name; Value
enum16 | ConnPh |  |  | Name: B; Value: 2
enum16 | ConnPh |  |  | Name: C; Value: 3

## 122
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Measurements_Status | 122 | uint16 |  |  | R | M | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 44 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | PVConn | PVConn |  | bitfield16 |  |  | R | M | PV inverter present/available status. Enumerated value.
Fixed Block |  | 3 | 1 | 1 | StorConn | StorConn |  | bitfield16 |  |  | R | M | Storage inverter present/available status. Enumerated value.
Fixed Block |  | 4 | 2 | 1 | ECPConn | ECPConn |  | bitfield16 |  |  | R | M | ECP connection status: disconnected=0 connected=1.
Fixed Block |  | 5 | 3 | 4 | ActWh | ActWh |  | acc64 | Wh |  | R | O | AC lifetime active (real) energy output.
Fixed Block |  | 9 | 7 | 4 | ActVAh | ActVAh |  | acc64 | VAh |  | R | O | AC lifetime apparent energy output.
Fixed Block |  | 13 | 11 | 4 | ActVArhQ1 | ActVArhQ1 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 1.
Fixed Block |  | 17 | 15 | 4 | ActVArhQ2 | ActVArhQ2 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 2.
Fixed Block |  | 21 | 19 | 4 | ActVArhQ3 | ActVArhQ3 |  | acc64 | varh |  | R | O | AC lifetime negative energy output in quadrant 3.
Fixed Block |  | 25 | 23 | 4 | ActVArhQ4 | ActVArhQ4 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 4.
Fixed Block |  | 29 | 27 | 1 | VArAval | VArAval |  | int16 | var | VArAval_SF | R | O | Amount of VARs available without impacting watts output.
Fixed Block |  | 30 | 28 | 1 | VArAval_SF | VArAval_SF |  | sunssf |  |  | R | O | Scale factor for available VARs.
Fixed Block |  | 31 | 29 | 1 | WAval | WAval |  | uint16 | var | WAval_SF | R | O | Amount of Watts available.
Fixed Block |  | 32 | 30 | 1 | WAval_SF | WAval_SF |  | sunssf |  |  | R | O | Scale factor for available Watts.
Fixed Block |  | 33 | 31 | 2 | StSetLimMsk | StSetLimMsk |  | bitfield32 |  |  | R | O | Bit Mask indicating setpoint limit(s) reached. | Bits shall be automatically cleared on read.
Fixed Block |  | 35 | 33 | 2 | StActCtl | StActCtl |  | bitfield32 |  |  | R | O | Bit Mask indicating which inverter controls are currently active.
Fixed Block |  | 37 | 35 | 4 | TmSrc | TmSrc |  | string |  |  | R | O | Source of time synchronization.
Fixed Block |  | 41 | 39 | 2 | Tms | Tms |  | uint32 | Secs |  | R | O | Seconds since 01-01-2000 00:00 UTC
Fixed Block |  | 43 | 41 | 1 | RtSt | RtSt |  | bitfield16 |  |  | R | O | Bit Mask indicating active ride-through status.
Fixed Block |  | 44 | 42 | 1 | Ris | Ris |  | uint16 | ohms | Ris_SF | R | O | Isolation resistance.
Fixed Block |  | 45 | 43 | 1 | Ris_SF | Ris_SF |  | sunssf |  |  | R | O | Scale factor for isolation resistance.
bitfield16 | PVConn |  |  | Name: CONNECTED; Value: 0
bitfield16 | PVConn |  |  | Name: AVAILABLE; Value: 1
bitfield16 | PVConn |  |  | Name: OPERATING; Value: 2
bitfield16 | PVConn |  |  | Name: TEST; Value: 3
bitfield16 | StorConn |  |  | Name: CONNECTED; Value: 0
bitfield16 | StorConn |  |  | Name: AVAILABLE; Value: 1
bitfield16 | StorConn |  |  | Name: OPERATING; Value: 2
bitfield16 | StorConn |  |  | Name: TEST; Value: 3
bitfield16 | ECPConn |  |  | Name: CONNECTED; Value: 0
bitfield32 | StSetLimMsk |  |  | Name: WMax; Value: 0
bitfield32 | StSetLimMsk |  |  | Name: VAMax; Value: 1
bitfield32 | StSetLimMsk |  |  | Name: VArAval; Value: 2
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ1; Value: 3
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ2; Value: 4
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ3; Value: 5
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ4; Value: 6
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ1; Value: 7
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ2; Value: 8
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ3; Value: 9
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ4; Value: 10
bitfield32 | StActCtl |  |  | Name: FixedW; Value: 0
bitfield32 | StActCtl |  |  | Name: FixedVAR; Value: 1
bitfield32 | StActCtl |  |  | Name: FixedPF; Value: 2
bitfield32 | StActCtl |  |  | Name: Volt-VAr; Value: 3
bitfield32 | StActCtl |  |  | Name: Freq-Watt-Param; Value: 4
bitfield32 | StActCtl |  |  | Name: Freq-Watt-Curve; Value: 5
bitfield32 | StActCtl |  |  | Name: Dyn-Reactive-Current; Value: 6
bitfield32 | StActCtl |  |  | Name: LVRT; Value: 7
bitfield32 | StActCtl |  |  | Name: HVRT; Value: 8
bitfield32 | StActCtl |  |  | Name: Watt-PF; Value: 9
bitfield32 | StActCtl |  |  | Name: Volt-Watt; Value: 10
bitfield32 | StActCtl |  |  | Name: Scheduled; Value: 12
bitfield32 | StActCtl |  |  | Name: LFRT; Value: 13
bitfield32 | StActCtl |  |  | Name: HFRT; Value: 14
bitfield16 | RtSt |  |  | Name: LVRT_ACTIVE; Value: 0
bitfield16 | RtSt |  |  | Name: HVRT_ACTIVE; Value: 1
bitfield16 | RtSt |  |  | Name: LFRT_ACTIVE; Value: 2
bitfield16 | RtSt |  |  | Name: HFRT_ACTIVE; Value: 3

## 123
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Immediate Controls | 123 | uint16 |  |  | R | M | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | RW | O | Time window for connect/disconnect.
Fixed Block |  | 3 | 1 | 1 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for connect/disconnect.
Fixed Block |  | 4 | 2 | 1 | Conn | Conn |  | enum16 |  |  | RW | M | Enumerated valued. Connection control.
Fixed Block |  | 5 | 3 | 1 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | RW | M | Set power output to specified level.
Fixed Block |  | 6 | 4 | 1 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for power limit change.
Fixed Block |  | 7 | 5 | 1 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power limit.
Fixed Block |  | 8 | 6 | 1 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 9 | 7 | 1 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Throttle enable/disable control.
Fixed Block |  | 10 | 8 | 1 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | RW | M | Set power factor to specific value - cosine of angle.
Fixed Block |  | 11 | 9 | 1 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | RW | O | Time window for power factor change.
Fixed Block |  | 12 | 10 | 1 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power factor.
Fixed Block |  | 13 | 11 | 1 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 14 | 12 | 1 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Fixed power factor enable/disable control.
Fixed Block |  | 15 | 13 | 1 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | RW | O | Reactive power in percent of WMax.
Fixed Block |  | 16 | 14 | 1 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | RW | O | Reactive power in percent of VArMax.
Fixed Block |  | 17 | 15 | 1 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | RW | O | Reactive power in percent of VArAval.
Fixed Block |  | 18 | 16 | 1 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for VAR limit change.
Fixed Block |  | 19 | 17 | 1 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for VAR limit.
Fixed Block |  | 20 | 18 | 1 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 21 | 19 | 1 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | RW | O | Enumerated value. VAR percent limit mode.
Fixed Block |  | 22 | 20 | 1 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Percent limit VAr enable/disable control.
Fixed Block |  | 23 | 21 | 1 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | R | M | Scale factor for power output percent.
Fixed Block |  | 24 | 22 | 1 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | R | M | Scale factor for power factor.
Fixed Block |  | 25 | 23 | 1 | VArPct_SF | VArPct_SF |  | sunssf |  |  | R | O | Scale factor for reactive power percent.
enum16 | Conn |  |  | Name: DISCONNECT; Value: 0
enum16 | Conn |  |  | Name: CONNECT; Value: 1
enum16 | WMaxLim_Ena |  |  | Name: DISABLED; Value: 0
enum16 | WMaxLim_Ena |  |  | Name: ENABLED; Value: 1
enum16 | OutPFSet_Ena |  |  | Name: DISABLED; Value: 0
enum16 | OutPFSet_Ena |  |  | Name: ENABLED; Value: 1
enum16 | VArPct_Mod |  |  | Name: NONE; Value: 0 |  | No VAR limit
enum16 | VArPct_Mod |  |  | Name: WMax; Value: 1 |  | VAR limit as a % of Wmax
enum16 | VArPct_Mod |  |  | Name: VArMax; Value: 2 |  | VAR limit as a % of VArMax
enum16 | VArPct_Mod |  |  | Name: VArAval; Value: 3 |  | VAR limit as a % of VArAval
enum16 | VArPct_Ena |  |  | Name: DISABLED; Value: 0
enum16 | VArPct_Ena |  |  | Name: ENABLED; Value: 1

## 124
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Storage | 124 | uint16 |  |  | R | M | Basic Storage Controls | Ref 3: 8.7.4.2
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WChaMax | WChaMax |  | uint16 | W | WChaMax_SF | RW | M | Setpoint for maximum charge.
Fixed Block |  | 3 | 1 | 1 | WChaGra | WChaGra |  | uint16 | % WChaMax/sec | WChaDisChaGra_SF | RW | M | Setpoint for maximum charging rate. Default is MaxChaRte.
Fixed Block |  | 4 | 2 | 1 | WDisChaGra | WDisChaGra |  | uint16 | % WChaMax/sec | WChaDisChaGra_SF | RW | M | Setpoint for maximum discharge rate. Default is MaxDisChaRte.
Fixed Block |  | 5 | 3 | 1 | StorCtl_Mod | StorCtl_Mod |  | bitfield16 |  |  | RW | M | Activate hold/discharge/charge storage control mode. Bitfield value.
Fixed Block |  | 6 | 4 | 1 | VAChaMax | VAChaMax |  | uint16 | VA | VAChaMax_SF | RW | O | Setpoint for maximum charging VA.
Fixed Block |  | 7 | 5 | 1 | MinRsvPct | MinRsvPct |  | uint16 | % WChaMax | MinRsvPct_SF | RW | O | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 8 | 6 | 1 | ChaState | ChaState |  | uint16 | % AhrRtg | ChaState_SF | R | O | Currently available energy as a percent of the capacity rating.
Fixed Block |  | 9 | 7 | 1 | StorAval | StorAval |  | uint16 | AH | StorAval_SF | R | O | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg).
Fixed Block |  | 10 | 8 | 1 | InBatV | InBatV |  | uint16 | V | InBatV_SF | R | O | Internal battery voltage.
Fixed Block |  | 11 | 9 | 1 | ChaSt | ChaSt |  | enum16 |  |  | R | O | Charge status of storage device. Enumerated value.
Fixed Block |  | 12 | 10 | 1 | OutWRte | OutWRte |  | int16 | % WDisChaMax | InOutWRte_SF | RW | O | Percent of max discharge rate.
Fixed Block |  | 13 | 11 | 1 | InWRte | InWRte |  | int16 | % WChaMax | InOutWRte_SF | RW | O | Percent of max charging rate.
Fixed Block |  | 14 | 12 | 1 | InOutWRte_WinTms | InOutWRte_WinTms |  | uint16 | Secs |  | RW | O | Time window for charge/discharge rate change.
Fixed Block |  | 15 | 13 | 1 | InOutWRte_RvrtTms | InOutWRte_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for charge/discharge rate.
Fixed Block |  | 16 | 14 | 1 | InOutWRte_RmpTms | InOutWRte_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 17 | 15 | Size: 1; Name: ChaGriSet; Type: enum16; R/W: RW | O
Fixed Block |  | 18 | 16 | 1 | WChaMax_SF | WChaMax_SF |  | sunssf |  |  | R | M | Scale factor for maximum charge.
Fixed Block |  | 19 | 17 | 1 | WChaDisChaGra_SF | WChaDisChaGra_SF |  | sunssf |  |  | R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 20 | 18 | 1 | VAChaMax_SF | VAChaMax_SF |  | sunssf |  |  | R | O | Scale factor for maximum charging VA.
Fixed Block |  | 21 | 19 | 1 | MinRsvPct_SF | MinRsvPct_SF |  | sunssf |  |  | R | O | Scale factor for minimum reserve percentage.
Fixed Block |  | 22 | 20 | 1 | ChaState_SF | ChaState_SF |  | sunssf |  |  | R | O | Scale factor for available energy percent.
Fixed Block |  | 23 | 21 | 1 | StorAval_SF | StorAval_SF |  | sunssf |  |  | R | O | Scale factor for state of charge.
Fixed Block |  | 24 | 22 | 1 | InBatV_SF | InBatV_SF |  | sunssf |  |  | R | O | Scale factor for battery voltage.
Fixed Block |  | 25 | 23 | 1 | InOutWRte_SF | InOutWRte_SF |  | sunssf |  |  | R | O | Scale factor for percent charge/discharge rate.
bitfield16 | StorCtl_Mod |  |  | Name: CHARGE; Value: 0
bitfield16 | StorCtl_Mod |  |  | Name: DiSCHARGE; Value: 1
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | ChaGriSet |  |  | Name: PV; Value: 0
enum16 | ChaGriSet |  |  | Name: GRID; Value: 1

## 125
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pricing | 125 | uint16 |  |  | R | M | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is price-based charge/dischage mode active?
Fixed Block |  | 3 | 1 | 1 | SigType | SigType |  | enum16 |  |  | RW | O | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description.
Fixed Block |  | 4 | 2 | 1 | Sig | Sig |  | int16 |  | Sig_SF | RW | M | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2.
Fixed Block |  | 5 | 3 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for charge/discharge pricing change.
Fixed Block |  | 6 | 4 | 1 | RvtTms | RvtTms |  | uint16 | Secs |  | RW | O | Timeout period for charge/discharge pricing change.
Fixed Block |  | 7 | 5 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current charge or discharge level to new level.
Fixed Block |  | 8 | 6 | 1 | Sig_SF | Sig_SF |  | sunssf |  |  | R | M | Pricing signal scale factor.
Fixed Block |  | 9 | 7 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | ModEna |  |  | Name: ENABLE; Value: 0
enum16 | SigType |  |  | Name: UNKNOWN; Value: 0 |  | Signal type is unknown or other type of value
enum16 | SigType |  |  | Name: ABSOLUTE; Value: 1 |  | Signal is an absolute price value in local rate. E.g. 23 (cents/kWh)
enum16 | SigType |  |  | Name: RELATIVE; Value: 2 |  | Signal is a relative price in local rate. E.g. -5 (cents/kWh)
enum16 | SigType |  |  | Name: MULTIPLIER; Value: 3 |  | Signal is a price multiplier (percentage). E.g. 15 % uplift in the rate
enum16 | SigType |  |  | Name: LEVEL; Value: 4 |  | Signal is a price level. E.g. 0=lowest 1=low 2=normal 3=high 4=highest

## 126
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Static Volt-VAR | 126 | uint16 |  |  | R | M | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-VAR control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-VAR change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-VAR curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | scale factor for dependent variable.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | VAr1 | VAr1 |  | int16 |  | DeptRef_SF | RW | M | Point 1 VARs.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | VAr2 | VAr2 |  | int16 |  | DeptRef_SF | RW | O | Point 2 VARs.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 19 | 7 | 1 | VAr3 | VAr3 |  | int16 | Various | DeptRef_SF | RW | O | Point 3 VARs.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 |  | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | VAr4 | VAr4 |  | int16 |  | DeptRef_SF | RW | O | Point 4 VARs.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | VAr5 | VAr5 |  | int16 |  | DeptRef_SF | RW | O | Point 5 VARs.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | VAr6 | VAr6 |  | int16 |  | DeptRef_SF | RW | O | Point 6 VARs.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | VAr7 | VAr7 |  | int16 |  | DeptRef_SF | RW | O | Point 7 VARs.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | VAr8 | VAr8 |  | int16 |  | DeptRef_SF | RW | O | Point 8 VARs.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | VAr9 | VAr9 |  | int16 |  | DeptRef_SF | RW | O | Point 9 VARs.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | VAr10 | VAr10 |  | int16 |  | DeptRef_SF | RW | O | Point 10 VARs.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | VAr11 | VAr11 |  | int16 |  | DeptRef_SF | RW | O | Point 11 VARs.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | VAr12 | VAr12 |  | int16 |  | DeptRef_SF | RW | O | Point 12 VARs.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | VAr13 | VAr13 |  | int16 |  | DeptRef_SF | RW | O | Point 13 VARs.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | VAr14 | VAr14 |  | int16 |  | DeptRef_SF | RW | O | Point 14 VARs.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | VAr15 | VAr15 |  | int16 |  | DeptRef_SF | RW | O | Point 15 VARs.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | VAr16 | VAr16 |  | int16 |  | DeptRef_SF | RW | O | Point 16 VARs.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | VAr17 | VAr17 |  | int16 |  | DeptRef_SF | RW | O | Point 17 VARs.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | VAr18 | VAr18 |  | int16 |  | DeptRef_SF | RW | O | Point 18 VARs.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | VAr19 | VAr19 |  | int16 |  | DeptRef_SF | RW | O | Point 19 VARs.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | VAr20 | VAr20 |  | int16 |  | DeptRef_SF | RW | O | Point 20 VARs.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 62 | 50 | 1 | RmpTms |  |  | uint16 | Secs |  | RW | O
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Boolean flag indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: WMax; Value: 1
enum16 | DeptRef |  |  | Name: VArMax; Value: 2
enum16 | DeptRef |  |  | Name: VArAval; Value: 3
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 127
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Freq-Watt Param | 127 | uint16 |  |  | R | M | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
Header |  | 1 |  | 1 | L |  | 10 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WGra | WGra |  | uint16 | % PM/Hz | WGra_SF | RW | M | The slope of the reduction in the maximum allowed watts output as a function of frequency.
Fixed Block |  | 3 | 1 | 1 | HzStr | HzStr |  | int16 | Hz | HzStrStop_SF | RW | M | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
Fixed Block |  | 4 | 2 | 1 | HzStop | HzStop |  | int16 | Hz | HzStrStop_SF | RW | M | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
Fixed Block |  | 5 | 3 | 1 | HysEna | HysEna |  | bitfield16 |  |  | RW | M | Enable hysterisis
Fixed Block |  | 6 | 4 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Parameterized Frequency-Watt control active.
Fixed Block |  | 7 | 5 | 1 | HzStopWGra | HzStopWGra |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
Fixed Block |  | 8 | 6 | 1 | WGra_SF | WGra_SF |  | sunssf |  |  | R | O | Scale factor for output gradient.
Fixed Block |  | 9 | 7 | 1 | HzStrStop_SF | HzStrStop_SF |  | sunssf |  |  | R | O | Scale factor for frequency deviations.
Fixed Block |  | 10 | 8 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | HysEna |  |  | Name: ENABLED; Value: 0
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0

## 128
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Dynamic Reactive Current | 128 | uint16 |  |  | R | M | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
Header |  | 1 |  | 1 | L |  | 14 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ArGraMod | ArGraMod |  | enum16 |  |  | RW | M | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband.
Fixed Block |  | 3 | 1 | 1 | ArGraSag | ArGraSag |  | uint16 | %ARtg/%dV | ArGra_SF | RW | M | The gradient used to increase capacitive dynamic current. A value of 0 indicates no additional reactive current support.
Fixed Block |  | 4 | 2 | 1 | ArGraSwell | ArGraSwell |  | uint16 | %ARtg/%dV | ArGra_SF | RW | M | The gradient used to increase inductive dynamic current. A value of 0 indicates no additional reactive current support.
Fixed Block |  | 5 | 3 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Activate dynamic reactive current model
Fixed Block |  | 6 | 4 | 1 | FilTms | FilTms |  | uint16 | Secs |  | RW | O | The time window used to calculate the moving average voltage.
Fixed Block |  | 7 | 5 | 1 | DbVMin | DbVMin |  | uint16 | % VRef | VRefPct_SF | RW | O | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced.
Fixed Block |  | 8 | 6 | 1 | DbVMax | DbVMax |  | uint16 | % VRef | VRefPct_SF | RW | O | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced.
Fixed Block |  | 9 | 7 | 1 | BlkZnV | BlkZnV |  | uint16 | % VRef | VRefPct_SF | RW | O | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced.
Fixed Block |  | 10 | 8 | 1 | HysBlkZnV | HysBlkZnV |  | uint16 | % VRef | VRefPct_SF | RW | O | Hysteresis voltage used with BlkZnV.
Fixed Block |  | 11 | 9 | 1 | BlkZnTmms | BlkZnTmms |  | uint16 | mSecs |  | RW | O | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops.
Fixed Block |  | 12 | 10 | 1 | HoldTmms | HoldTmms |  | uint16 | mSecs |  | RW | O | Hold time during which reactive current support continues after the average voltage has entered the dead zone.
Fixed Block |  | 13 | 11 | 1 | ArGra_SF | ArGra_SF |  | sunssf |  |  | R | M | Scale factor for the gradients.
Fixed Block |  | 14 | 12 | 1 | VRefPct_SF | VRefPct_SF |  | sunssf |  |  | R | O | Scale factor for the voltage zone and limit settings.
Fixed Block |  | 15 | 13 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | ArGraMod |  |  | Name: EDGE; Value: 0
enum16 | ArGraMod |  |  | Name: CENTER; Value: 1
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0

## 129
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTD | 129 | uint16 |  |  | R | M | LVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 130
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTD | 130 | uint16 |  |  | R | M | HVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 131
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Watt-PF | 131 | uint16 |  |  | R | M | Watt-Power Factor | Ref 3: 8.11.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is watt-PF mode active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for watt-PF change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for watt-PF curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Max number of points in array.
Fixed Block |  | 9 | 7 | 1 | W_SF | W_SF |  | sunssf |  |  | R | M | Scale factor for percent WMax.
Fixed Block |  | 10 | 8 | 1 | PF_SF | PF_SF |  | sunssf |  |  | R | M | Scale factor for PF.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | W1 | W1 |  | int16 | % WMax | W_SF | RW | M | Point 1 Watts.
Repeating Block |  | 14 | 2 | 1 | PF1 | PF1 |  | int16 | cos() | PF_SF | RW | M | Point 1 PF in EEI notation.
Repeating Block |  | 15 | 3 | 1 | W2 | W2 |  | int16 | % WMax | W_SF | RW | O | Point 2 Watts.
Repeating Block |  | 16 | 4 | 1 | PF2 | PF2 |  | int16 | cos() | PF_SF | RW | O | Point 2 PF in EEI notation.
Repeating Block |  | 17 | 5 | 1 | W3 | W3 |  | int16 | % WMax | W_SF | RW | O | Point 3 Watts.
Repeating Block |  | 18 | 6 | 1 | PF3 | PF3 |  | int16 | cos() | PF_SF | RW | O | Point 3 PF in EEI notation.
Repeating Block |  | 19 | 7 | 1 | W4 | W4 |  | int16 | % WMax | W_SF | RW | O | Point 4 Watts.
Repeating Block |  | 20 | 8 | 1 | PF4 | PF4 |  | int16 | cos() | PF_SF | RW | O | Point 4 PF in EEI notation.
Repeating Block |  | 21 | 9 | 1 | W5 | W5 |  | int16 | % WMax | W_SF | RW | O | Point 5 Watts.
Repeating Block |  | 22 | 10 | 1 | PF5 | PF5 |  | int16 | cos() | PF_SF | RW | O | Point 5 PF in EEI notation.
Repeating Block |  | 23 | 11 | 1 | W6 | W6 |  | int16 | % WMax | W_SF | RW | O | Point 6 Watts.
Repeating Block |  | 24 | 12 | 1 | PF6 | PF6 |  | int16 | cos() | PF_SF | RW | O | Point 6 PF in EEI notation.
Repeating Block |  | 25 | 13 | 1 | W7 | W7 |  | int16 | % WMax | W_SF | RW | O | Point 7 Watts.
Repeating Block |  | 26 | 14 | 1 | PF7 | PF7 |  | int16 | cos() | PF_SF | RW | O | Point 7 PF in EEI notation.
Repeating Block |  | 27 | 15 | 1 | W8 | W8 |  | int16 | % WMax | W_SF | RW | O | Point 8 Watts.
Repeating Block |  | 28 | 16 | 1 | PF8 | PF8 |  | int16 | cos() | PF_SF | RW | O | Point 8 PF in EEI notation.
Repeating Block |  | 29 | 17 | 1 | W9 | W9 |  | int16 | % WMax | W_SF | RW | O | Point 9 Watts.
Repeating Block |  | 30 | 18 | 1 | PF9 | PF9 |  | int16 | cos() | PF_SF | RW | O | Point 9 PF in EEI notation.
Repeating Block |  | 31 | 19 | 1 | W10 | W10 |  | int16 | % WMax | W_SF | RW | O | Point 10 Watts.
Repeating Block |  | 32 | 20 | 1 | PF10 | PF10 |  | int16 | cos() | PF_SF | RW | O | Point 10 PF in EEI notation.
Repeating Block |  | 33 | 21 | 1 | W11 | W11 |  | int16 | % WMax | W_SF | RW | O | Point 11 Watts.
Repeating Block |  | 34 | 22 | 1 | PF11 | PF11 |  | int16 | cos() | PF_SF | RW | O | Point 11 PF in EEI notation.
Repeating Block |  | 35 | 23 | 1 | W12 | W12 |  | int16 | % WMax | W_SF | RW | O | Point 12 Watts.
Repeating Block |  | 36 | 24 | 1 | PF12 | PF12 |  | int16 | cos() | PF_SF | RW | O | Point 12 PF in EEI notation.
Repeating Block |  | 37 | 25 | 1 | W13 | W13 |  | int16 | % WMax | W_SF | RW | O | Point 13 Watts.
Repeating Block |  | 38 | 26 | 1 | PF13 | PF13 |  | int16 | cos() | PF_SF | RW | O | Point 13 PF in EEI notation.
Repeating Block |  | 39 | 27 | 1 | W14 | W14 |  | int16 | % WMax | W_SF | RW | O | Point 14 Watts.
Repeating Block |  | 40 | 28 | 1 | PF14 | PF14 |  | int16 | cos() | PF_SF | RW | O | Point 14 PF in EEI notation.
Repeating Block |  | 41 | 29 | 1 | W15 | W15 |  | int16 | % WMax | W_SF | RW | O | Point 15 Watts.
Repeating Block |  | 42 | 30 | 1 | PF15 | PF15 |  | int16 | cos() | PF_SF | RW | O | Point 15 PF in EEI notation.
Repeating Block |  | 43 | 31 | 1 | W16 | W16 |  | int16 | % WMax | W_SF | RW | O | Point 16 Watts.
Repeating Block |  | 44 | 32 | 1 | PF16 | PF16 |  | int16 | cos() | PF_SF | RW | O | Point 16 PF in EEI notation.
Repeating Block |  | 45 | 33 | 1 | W17 | W17 |  | int16 | % WMax | W_SF | RW | O | Point 17 Watts.
Repeating Block |  | 46 | 34 | 1 | PF17 | PF17 |  | int16 | cos() | PF_SF | RW | O | Point 17 PF in EEI notation.
Repeating Block |  | 47 | 35 | 1 | W18 | W18 |  | int16 | % WMax | W_SF | RW | O | Point 18 Watts.
Repeating Block |  | 48 | 36 | 1 | PF18 | PF18 |  | int16 | cos() | PF_SF | RW | O | Point 18 PF in EEI notation.
Repeating Block |  | 49 | 37 | 1 | W19 | W19 |  | int16 | % WMax | W_SF | RW | O | Point 19 Watts.
Repeating Block |  | 50 | 38 | 1 | PF19 | PF19 |  | int16 | cos() | PF_SF | RW | O | Point 19 PF in EEI notation.
Repeating Block |  | 51 | 39 | 1 | W20 | W20 |  | int16 | % WMax | W_SF | RW | O | Point 20 Watts.
Repeating Block |  | 52 | 40 | 1 | PF20 | PF20 |  | int16 | cos() | PF_SF | RW | O | Point 20 PF in EEI notation.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | RmpPT1Tms | RmpPT1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 62 | 50 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % PF/min | RmpIncDec_SF | RW | O | The maximum rate at which the power factor may be reduced in response to changes in the power value.
Repeating Block |  | 63 | 51 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % PF/min | RmpIncDec_SF | RW | O | The maximum rate at which the power factor may be increased in response to changes in the power value.
Repeating Block |  | 64 | 52 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
Repeating Block |  | 65 | 53 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 132
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Volt-Watt | 132 | uint16 |  |  | R | M | Volt-Watt | Ref 3: 8.12.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of points in array (maximum 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | Scale Factor for % DeptRef
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | W1 | W1 |  | int16 | % VRef | DeptRef_SF | RW | M | Point 1 Watts.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | W2 | W2 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 2 Watts.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 Volts.
Repeating Block |  | 19 | 7 | 1 | W3 | W3 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 3 Watts.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | W4 | W4 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 4 Watts.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | W5 | W5 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 5 Watts.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | W6 | W6 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 6 Watts.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | W7 | W7 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 7 Watts.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | W8 | W8 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 8 Watts.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | W9 | W9 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 9 Watts.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | W10 | W10 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 10 Watts.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | W11 | W11 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 11 Watts.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | W12 | W12 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 12 Watts.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | W13 | W13 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 13 Watts.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | W14 | W14 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 14 Watts.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | W15 | W15 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 15 Watts.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | W16 | W16 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 16 Watts.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | W17 | W17 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 17 Watts.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | W18 | W18 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 18 Watts.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | W19 | W19 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 19 Watts.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | W20 | W20 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 20 Watts.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 62 | 50 | 1 | RmpPt1Tms | RmpPt1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: %WMax; Value: 1
enum16 | DeptRef |  |  | Name: %WAval; Value: 2
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 133
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Scheduling | 133 | uint16 |  |  | R | M | Basic Scheduling | Ref 2: 2.2.8
Header |  | 1 |  | 1 | L |  | 6 + (RB Count * 60) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | ActSchd | ActSchd |  | bitfield32 |  |  | RW | M | Bitfield of active schedules
Fixed Block |  | 4 | 2 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is basic scheduling active.
Fixed Block |  | 5 | 3 | 1 | NSchd | NSchd |  | uint16 |  |  | R | M | Number of schedules supported (recommend min. 4, max 32)
Fixed Block |  | 6 | 4 | 1 | NPts | NPts |  | uint16 |  |  | R | M | Number of schedule entries supuported (maximum of 10).
Fixed Block |  | 7 | 5 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
Repeating Block |  | 8 | 0 | 1 | ActPts | ActPts |  | uint16 |  |  | RW | M | Number of active entries in schedule.
Repeating Block |  | 9 | 1 | 2 | StrTms | StrTms |  | uint32 | Secs |  | RW | M | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC.
Repeating Block |  | 11 | 3 | 1 | RepPer | RepPer |  | uint16 |  |  | RW | M | The repetition count for time-based schedules (0=repeat forever)
Repeating Block |  | 12 | 4 | 1 | IntvTyp | SchdTyp |  | enum16 |  |  | RW | M | The repetition frequency for time-based schedules: no repeat=0
Repeating Block |  | 13 | 5 | 1 | XTyp | XTyp |  | enum16 |  |  | RW | M | The meaning of the X-values in the array.
Repeating Block |  | 14 | 6 | 1 | X_SF | X_SF |  | sunssf |  |  | RW | M | Scale factor for schedule range values.
Repeating Block |  | 15 | 7 | 1 | YTyp | YTyp |  | enum16 |  |  | RW | M | The meaning of the Y-values in the array.
Repeating Block |  | 16 | 8 | 1 | Y_SF | Y_SF |  | sunssf |  |  | RW | M | Scale factor for schedule target values.
Repeating Block |  | 17 | 9 | 2 | X1 | X1 |  | int32 |  | X_SF | RW | M | Entry 1 range.
Repeating Block |  | 19 | 11 | 2 | Y1 | Y1 |  | int32 |  | Y_SF | RW | M | Entry 1 target.
Repeating Block |  | 21 | 13 | 2 | X2 | X2 |  | int32 |  | X_SF | RW | O | Entry 2 range.
Repeating Block |  | 23 | 15 | 2 | Y2 | Y2 |  | int32 |  | Y_SF | RW | O | Entry 2 target.
Repeating Block |  | 25 | 17 | 2 | X3 | X3 |  | int32 |  | X_SF | RW | O | Entry 3 range.
Repeating Block |  | 27 | 19 | 2 | Y3 | Y3 |  | int32 |  | Y_SF | RW | O | Entry 3 target.
Repeating Block |  | 29 | 21 | 2 | X4 | X4 |  | int32 |  | X_SF | RW | O | Entry 4 range.
Repeating Block |  | 31 | 23 | 2 | Y4 | Y4 |  | int32 |  | Y_SF | RW | O | Entry 4 target.
Repeating Block |  | 33 | 25 | 2 | X5 | X5 |  | int32 |  | X_SF | RW | O | Entry 15range.
Repeating Block |  | 35 | 27 | 2 | Y5 | Y5 |  | int32 |  | Y_SF | RW | O | Entry 5 target.
Repeating Block |  | 37 | 29 | 2 | X6 | X6 |  | int32 |  | X_SF | RW | O | Entry 6 range.
Repeating Block |  | 39 | 31 | 2 | Y6 | Y6 |  | int32 |  | Y_SF | RW | O | Entry 6 target.
Repeating Block |  | 41 | 33 | 2 | X7 | X7 |  | int32 |  | X_SF | RW | O | Entry 7 range.
Repeating Block |  | 43 | 35 | 2 | Y7 | Y7 |  | int32 |  | Y_SF | RW | O | Entry 7 target.
Repeating Block |  | 45 | 37 | 2 | X8 | X8 |  | int32 |  | X_SF | RW | O | Entry 8 range.
Repeating Block |  | 47 | 39 | 2 | Y8 | Y8 |  | int32 |  | Y_SF | RW | O | Entry 8 target.
Repeating Block |  | 49 | 41 | 2 | X9 | X9 |  | int32 |  | X_SF | RW | O | Entry 9 range.
Repeating Block |  | 51 | 43 | 2 | Y9 | Y9 |  | int32 |  | Y_SF | RW | O | Entry 9 target.
Repeating Block |  | 53 | 45 | 2 | X10 | X10 |  | int32 |  | X_SF | RW | O | Entry 10 range.
Repeating Block |  | 55 | 47 | 2 | Y10 | Y10 |  | int32 |  | Y_SF | RW | O | Entry 10 target.
Repeating Block |  | 57 | 49 | 8 | Nam | Nam |  | string |  |  | RW | O | Optional description for schedule.
Repeating Block |  | 65 | 57 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for schedule entry change.
Repeating Block |  | 66 | 58 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current target to new target.
Repeating Block |  | 67 | 59 | 1 | ActIndx | ActIndx |  | uint16 |  |  | R | M | Index of active entry in the active schedule.
bitfield32 | ActSchd |  |  | Name: SCHED1; Value: 0
bitfield32 | ActSchd |  |  | Name: SCHED2; Value: 1
bitfield32 | ActSchd |  |  | Name: SCHED3; Value: 2
bitfield32 | ActSchd |  |  | Name: SCHED4; Value: 3
bitfield32 | ActSchd |  |  | Name: SCHED5; Value: 4
bitfield32 | ActSchd |  |  | Name: SCHED6; Value: 5
bitfield32 | ActSchd |  |  | Name: SCHED7; Value: 6
bitfield32 | ActSchd |  |  | Name: SCHED8; Value: 7
bitfield32 | ActSchd |  |  | Name: SCHED9; Value: 8
bitfield32 | ActSchd |  |  | Name: SCHED10; Value: 9
bitfield32 | ActSchd |  |  | Name: SCHED12; Value: 10
bitfield32 | ActSchd |  |  | Name: SCHED13; Value: 11
bitfield32 | ActSchd |  |  | Name: SCHED14; Value: 12
bitfield32 | ActSchd |  |  | Name: SCHED15; Value: 13
bitfield32 | ActSchd |  |  | Name: SCHED16; Value: 14
bitfield32 | ActSchd |  |  | Name: SCHED17; Value: 15
bitfield32 | ActSchd |  |  | Name: SCHED18; Value: 16
bitfield32 | ActSchd |  |  | Name: SCHED19; Value: 17
bitfield32 | ActSchd |  |  | Name: SCHED20; Value: 18
bitfield32 | ActSchd |  |  | Name: SCHED21; Value: 19
bitfield32 | ActSchd |  |  | Name: SCHED22; Value: 21
bitfield32 | ActSchd |  |  | Name: SCHED23; Value: 22
bitfield32 | ActSchd |  |  | Name: SCHED24; Value: 23
bitfield32 | ActSchd |  |  | Name: SCHED25; Value: 24
bitfield32 | ActSchd |  |  | Name: SCHED26; Value: 25
bitfield32 | ActSchd |  |  | Name: SCHED27; Value: 26
bitfield32 | ActSchd |  |  | Name: SCHED28; Value: 27
bitfield32 | ActSchd |  |  | Name: SCHED29; Value: 28
bitfield32 | ActSchd |  |  | Name: SCHED30; Value: 29
bitfield32 | ActSchd |  |  | Name: SCHED31; Value: 30
bitfield32 | ActSchd |  |  | Name: SCHED32; Value: 31
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | IntvTyp |  |  | Name: ONETIME; Value: 0
enum16 | IntvTyp |  |  | Name: DAILY; Value: 1
enum16 | IntvTyp |  |  | Name: WEEKLY; Value: 2
enum16 | IntvTyp |  |  | Name: MONTHLY; Value: 3
enum16 | IntvTyp |  |  | Name: WEEKDAY; Value: 4
enum16 | IntvTyp |  |  | Name: HOLIDAY; Value: 5
enum16 | IntvTyp |  |  | Name: WEEKEND; Value: 6
enum16 | IntvTyp |  |  | Name: YEARLY; Value: 7
enum16 | XTyp |  |  | Name: UNSET; Value: 0
enum16 | XTyp |  |  | Name: TIME; Value: 1
enum16 | XTyp |  |  | Name: TEMP; Value: 2
enum16 | XTyp |  |  | Name: PRICE; Value: 3
enum16 | XTyp |  |  | Name: OTHER; Value: 99
enum16 | YTyp |  |  | Name: UNSET; Value: 0
enum16 | YTyp |  |  | Name: WMax; Value: 1
enum16 | YTyp |  |  | Name: RSRVD2; Value: 2
enum16 | YTyp |  |  | Name: PF; Value: 3
enum16 | YTyp |  |  | Name: RSRVD4; Value: 4
enum16 | YTyp |  |  | Name: WATT_PRICE; Value: 5
enum16 | YTyp |  |  | Name: VAR_PRICE; Value: 6
enum16 | YTyp |  |  | Name: RSRVD7; Value: 7
enum16 | YTyp |  |  | Name: VOLT_VAR_ARRAY; Value: 8
enum16 | YTyp |  |  | Name: WChaGra; Value: 9
enum16 | YTyp |  |  | Name: WDisChaGra; Value: 10
enum16 | YTyp |  |  | Name: VArAval; Value: 11
enum16 | YTyp |  |  | Name: Schedule; Value: 12
enum16 | YTyp |  |  | Name: OTHER; Value: 99

## 134
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Freq-Watt Crv | 134 | uint16 |  |  | R | M | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 58) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is curve-based Frequency-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for freq-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for freq-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 10).
Fixed Block |  | 9 | 7 | 1 | Hz_SF | Hz_SF |  | sunssf | SF |  | R | M | Scale factor for frequency.
Fixed Block |  | 10 | 8 | 1 | W_SF | W_SF |  | sunssf | SF |  | R | M | Scale factor for percent WRef.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf | SF |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 Hertz.
Repeating Block |  | 14 | 2 | 1 | W1 | W1 |  | int16 | % WRef | W_SF | RW | M | Point 1 Watts.
Repeating Block |  | 15 | 3 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 Hertz.
Repeating Block |  | 16 | 4 | 1 | W2 | W2 |  | int16 | % WRef | W_SF | RW | O | Point 2 Watts.
Repeating Block |  | 17 | 5 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 Hertz.
Repeating Block |  | 18 | 6 | 1 | W3 | W3 |  | int16 | % WRef | W_SF | RW | O | Point 3 Watts.
Repeating Block |  | 19 | 7 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 Hertz.
Repeating Block |  | 20 | 8 | 1 | W4 | W4 |  | int16 | % WRef | W_SF | RW | O | Point 4 Watts.
Repeating Block |  | 21 | 9 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 Hertz.
Repeating Block |  | 22 | 10 | 1 | W5 | W5 |  | int16 | % WRef | W_SF | RW | O | Point 5 Watts.
Repeating Block |  | 23 | 11 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 Hertz.
Repeating Block |  | 24 | 12 | 1 | W6 | W6 |  | int16 | % WRef | W_SF | RW | O | Point 6 Watts.
Repeating Block |  | 25 | 13 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 Hertz.
Repeating Block |  | 26 | 14 | 1 | W7 | W7 |  | int16 | % WRef | W_SF | RW | O | Point 7 Watts.
Repeating Block |  | 27 | 15 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 Hertz.
Repeating Block |  | 28 | 16 | 1 | W8 | W8 |  | int16 | % WRef | W_SF | RW | O | Point 8 Watts.
Repeating Block |  | 29 | 17 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 Hertz.
Repeating Block |  | 30 | 18 | 1 | W9 | W9 |  | int16 | % WRef | W_SF | RW | O | Point 9 Watts.
Repeating Block |  | 31 | 19 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 Hertz.
Repeating Block |  | 32 | 20 | 1 | W10 | W10 |  | int16 | % WRef | W_SF | RW | O | Point 10 Watts.
Repeating Block |  | 33 | 21 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 Hertz.
Repeating Block |  | 34 | 22 | 1 | W11 | W11 |  | int16 | % WRef | W_SF | RW | O | Point 11 Watts.
Repeating Block |  | 35 | 23 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 Hertz.
Repeating Block |  | 36 | 24 | 1 | W12 | W12 |  | int16 | % WRef | W_SF | RW | O | Point 12 Watts.
Repeating Block |  | 37 | 25 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 Hertz.
Repeating Block |  | 38 | 26 | 1 | W13 | W13 |  | int16 | % WRef | W_SF | RW | O | Point 13 Watts.
Repeating Block |  | 39 | 27 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 Hertz.
Repeating Block |  | 40 | 28 | 1 | W14 | W14 |  | int16 | % WRef | W_SF | RW | O | Point 14 Watts.
Repeating Block |  | 41 | 29 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 Hertz.
Repeating Block |  | 42 | 30 | 1 | W15 | W15 |  | int16 | % WRef | W_SF | RW | O | Point 15 Watts.
Repeating Block |  | 43 | 31 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 Hertz.
Repeating Block |  | 44 | 32 | 1 | W16 | W16 |  | int16 | % WRef | W_SF | RW | O | Point 16 Watts.
Repeating Block |  | 45 | 33 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 Hertz.
Repeating Block |  | 46 | 34 | 1 | W17 | W17 |  | int16 | % WRef | W_SF | RW | O | Point 17 Watts.
Repeating Block |  | 47 | 35 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 Hertz.
Repeating Block |  | 48 | 36 | 1 | W18 | W18 |  | int16 | % WRef | W_SF | RW | O | Point 18 Watts.
Repeating Block |  | 49 | 37 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 Hertz.
Repeating Block |  | 50 | 38 | 1 | W19 | W19 |  | int16 | % WRef | W_SF | RW | O | Point 19 Watts.
Repeating Block |  | 51 | 39 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 Hertz.
Repeating Block |  | 52 | 40 | 1 | W20 | W20 |  | int16 | % WRef | W_SF | RW | O | Point 20 Watts.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 61 | 49 | 1 | RmpPT1Tms | RmpPT1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 62 | 50 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be reduced in response to changes in the frequency value.
Repeating Block |  | 63 | 51 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be increased in response to changes in the frequency value.
Repeating Block |  | 64 | 52 | 1 | RmpRsUp | RmpRsUp |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function.
Repeating Block |  | 65 | 53 | 1 | SnptW | SnptW |  | bitfield16 |  |  | RW | M | 1=enable snapshot/capture mode
Repeating Block |  | 66 | 54 | 1 | WRef | WRef |  | uint16 | W | W_SF | RW | O | Reference active power (default = WMax).
Repeating Block |  | 67 | 55 | 1 | WRefStrHz | WRefStrHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output.
Repeating Block |  | 68 | 56 | 1 | WRefStopHz | WRefStopHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at which to release the power output.
Repeating Block |  | 69 | 57 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 135
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRT | 135 | uint16 |  |  | R | M | Low Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 136
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HFRT | 136 | uint16 |  |  | R | M | High Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HFRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HFRT change. | Setting is ignored for HFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HFRT curve selection. | Setting is ignored for HFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 137
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTC | 137 | uint16 |  |  | R | M | LVRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must remain connected voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must remain connected voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must remain connected voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must remain connected voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must remain connected voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must remain connected voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must remain connected voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must remain connected voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must remain connected voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must remain connected voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must remain connected voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must remain connected voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must remain connected voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must remain connected voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must remain connected voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must remain connected voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must remain connected voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must remain connected voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must remain connected voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must remain connected voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 138
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTC | 138 | uint16 |  |  | R | M | HVRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must remain connected voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must remain connected voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must remain connected voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must remain connected voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must remain connected voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must remain connected voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must remain connected voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must remain connected voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must remain connected voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must remain connected voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must remain connected voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must remain connected voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must remain connected voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must remain connected voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must remain connected voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must remain connected voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must remain connected voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must remain connected voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must remain connected voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must remain connected voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 139
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTX | 139 | uint16 |  |  | R | M | LVRT extended curve | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: CrvType; Type: enum16; R/W: R | M
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | CrvType |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 140
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTX | 140 | uint16 |  |  | R | M | HVRT extended curve | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: CrvType; Type: enum16; R/W: R | M
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | CrvType |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 141
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRTC | 141 | uint16 |  |  | R | M | LFRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must remain connected frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must remain connected frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must remain connected frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must remain connected frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must remain connected frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must remain connected frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must remain connected frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must remain connected frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must remain connected frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must remain connected frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must remain connected frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must remain connected frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must remain connected frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must remain connected frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must remain connected frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must remain connected frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must remain connected frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must remain connected frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must remain connected frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must remain connected frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 142
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HFRTC | 142 | uint16 |  |  | R | M | HFRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must remain connected frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must remain connected frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must remain connected frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must remain connected frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must remain connected frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must remain connected frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must remain connected frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must remain connected frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must remain connected frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must remain connected frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must remain connected frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must remain connected frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must remain connected frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must remain connected frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must remain connected frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must remain connected frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must remain connected frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must remain connected frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must remain connected frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must remain connected frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 143
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRTX | 143 | uint16 |  |  | R | M | LFRT extended curve | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: CrvType; Type: enum16; R/W: R | M
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | CrvType |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 144
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HFRTX | 144 | uint16 |  |  | R | M | HFRT extended curve | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: CrvType; Type: enum16; R/W: R | M
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | CrvType |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 145
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Extended Settings | 145 | uint16 |  |  | R | M | Inverter controls extended settings
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | NomRmpUpRte | Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Ramp up rate as a percentage of max current.
Fixed Block |  | 3 | 1 | 1 | NomRmpDnRte | NomRmpDnRte |  | uint16 | Pct | Rmp_SF | RW | O | Ramp down rate as a percentage of max current.
Fixed Block |  | 4 | 2 | 1 | EmgRmpUpRte | Emergency Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Emergency ramp up rate as a percentage of max current.
Fixed Block |  | 5 | 3 | 1 | EmgRmpDnRte | Emergency Ramp Down Rate |  | uint16 | Pct | Rmp_SF | RW | O | Emergency ramp down rate as a percentage of max current.
Fixed Block |  | 6 | 4 | 1 | ConnRmpUpRte | Connect Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Connect ramp up rate as a percentage of max current.
Fixed Block |  | 7 | 5 | 1 | ConnRmpDnRte | Connect Ramp Down Rate |  | uint16 | Pct | Rmp_SF | RW | O | Connect ramp down rate as a percentage of max current.
Fixed Block |  | 8 | 6 | 1 | AGra | Default Ramp Rate |  | uint16 | Pct | Rmp_SF | RW | O | Ramp rate specified in percent of max current.
Fixed Block |  | 9 | 7 | 1 | Rmp_SF | Ramp Rate Scale Factor |  | sunssf |  |  | R | O | Ramp Rate Scale Factor

## 160
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Multiple MPPT Inverter Extension Model | 160 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 8 + (RB Count * 20) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DCA_SF | Current Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 3 | 1 | 1 | DCV_SF | Voltage Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 4 | 2 | 1 | DCW_SF | Power Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 5 | 3 | 1 | DCWH_SF | Energy Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 6 | 4 | 2 | Evt | Global Events |  | bitfield32 |  |  | R | O
Fixed Block |  | 8 | 6 | 1 | N | Number of Modules |  | count |  |  | R | O
Fixed Block |  | 9 | 7 | 1 | TmsPer | Timestamp Period |  | uint16 |  |  | R | O
Repeating Block |  | 10 | 0 | 1 | ID | Input ID |  | uint16 |  |  | R | O
Repeating Block |  | 11 | 1 | 8 | IDStr | Input ID Sting |  | string |  |  | R | O
Repeating Block |  | 19 | 9 | 1 | DCA | DC Current |  | uint16 | A | DCA_SF | R | O
Repeating Block |  | 20 | 10 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O
Repeating Block |  | 21 | 11 | 1 | DCW | DC Power |  | uint16 | W | DCW_SF | R | O
Repeating Block |  | 22 | 12 | 2 | DCWH | Lifetime Energy |  | acc32 | Wh | DCWH_SF | R | O
Repeating Block |  | 24 | 14 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O
Repeating Block |  | 26 | 16 | 1 | Tmp | Temperature |  | int16 | C |  | R | O
Repeating Block |  | 27 | 17 | 1 | DCSt | Operating State |  | enum16 |  |  | R | O
Repeating Block |  | 28 | 18 | 2 | DCEvt | Module Events |  | bitfield32 |  |  | R | O
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Input Over Voltage; Value: 1
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: DC Disconnect; Value: 3
bitfield32 | Evt |  |  | Name: CABINET_OPEN; Label: Cabinet Open; Value: 5
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual Shutdown; Value: 6
bitfield32 | Evt |  |  | Name: OVER_TEMP; Label: Over Temperature; Value: 7
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12
bitfield32 | Evt |  |  | Name: UNDER_TEMP; Label: Under Temperature; Value: 13
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20
bitfield32 | Evt |  |  | Name: INPUT_UNDER_VOLTAGE; Label: Under Voltage; Value: 21
bitfield32 | Evt |  |  | Name: INPUT_OVER_CURRENT; Label: Over Current; Value: 22
enum16 | DCSt |  |  | Name: OFF; Label: Off; Value: 1
enum16 | DCSt |  |  | Name: SLEEPING; Label: Sleeping; Value: 2
enum16 | DCSt |  |  | Name: STARTING; Label: Starting; Value: 3
enum16 | DCSt |  |  | Name: MPPT; Label: MPPT; Value: 4
enum16 | DCSt |  |  | Name: THROTTLED; Label: Throttled; Value: 5
enum16 | DCSt |  |  | Name: SHUTTING_DOWN; Label: Shutting Down; Value: 6
enum16 | DCSt |  |  | Name: FAULT; Label: Fault; Value: 7
enum16 | DCSt |  |  | Name: STANDBY; Label: Standby; Value: 8
enum16 | DCSt |  |  | Name: TEST; Label: Test; Value: 9
enum16 | DCSt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | DCEvt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0
bitfield32 | DCEvt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Input Over Voltage; Value: 1
bitfield32 | DCEvt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | DCEvt |  |  | Name: DC_DISCONNECT; Label: DC Disconnect; Value: 3
bitfield32 | DCEvt |  |  | Name: CABINET_OPEN; Label: Cabinet Open; Value: 5
bitfield32 | DCEvt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual Shutdown; Value: 6
bitfield32 | DCEvt |  |  | Name: OVER_TEMP; Label: Over Temperature; Value: 7
bitfield32 | DCEvt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12
bitfield32 | DCEvt |  |  | Name: UNDER_TEMP; Label: Under Temperature; Value: 13
bitfield32 | DCEvt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14
bitfield32 | DCEvt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15
bitfield32 | DCEvt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20
bitfield32 | DCEvt |  |  | Name: INPUT_UNDER_VOLTAGE; Label: Under Voltage; Value: 21
bitfield32 | DCEvt |  |  | Name: INPUT_OVER_CURRENT; Label: Over Current; Value: 22

## 201
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Meter (Single Phase)single phase (AN or AB) meter | 201 | uint16 |  |  | R | M | Include this model for single phase (AN or AB) metering
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | O | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | O | Line to Neutral AC Voltage (average of active phases) | Conditional AN connection
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | O | Phase Voltage AN | Conditional AN connection
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | O | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PPVphAB | Phase Voltage AB |  | int16 | V | V_SF | R | O | Phase Voltage AB | Conditional AB connection
Fixed Block |  | 13 | 11 | 1 | PPVphBC | Phase Voltage BC |  | int16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 1 | PPVphCA | Phase Voltage CA |  | int16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: Power_Failure; Label: Power Failure; Value: 2 |  | Loss of power or phase
bitfield32 | Evt |  |  | Name: Under_Voltage; Label: Under Voltage; Value: 3 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Name: Low_PF; Label: Low PF; Value: 4 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Name: Over_Current; Label: Over Current; Value: 5 |  | Current Input over threshold
bitfield32 | Evt |  |  | Name: Over_Voltage; Label: Over Voltage; Value: 6 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Name: Missing_Sensor; Label: Missing Sensor; Value: 7 |  | Sensor not connected
bitfield32 | Evt |  |  | Name: OEM01; Label: OEM01; Value: 16 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM02; Label: OEM02; Value: 17 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM03; Label: OEM01; Value: 18 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM04; Label: OEM04; Value: 19 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM05; Label: OEM05; Value: 20 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM06; Label: OEM06; Value: 21 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM07; Label: OEM07; Value: 22 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM08; Label: OEM08; Value: 23 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM09; Label: OEM09; Value: 24 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM10; Label: OEM10; Value: 25 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM11; Label: OEM11; Value: 26 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM12; Label: OEM12; Value: 27 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM13; Label: OEM13; Value: 28 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM14; Label: OEM14; Value: 29 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM15; Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 202
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | split single phase (ABN) meter | 202 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | O | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | O
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | O
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB | Total VAr-hours Exported Q4 Imported phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 203
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | wye-connect three phase (abcn) meter | 203 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | M | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 204
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | delta-connect three phase (abc) meter | 204 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | O | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 211
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | single phase (AN or AB) meter | 211 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | O | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | O | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | O | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 212
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | split single phase (ABN) meter | 212 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 213
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | wye-connect three phase (abcn) meter | 213 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | M | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | M | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | M | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 214
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | delta-connect three phase (abc) meter | 214 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | O | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | M | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | M | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 220
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure AC Meter Selected Readings | 220 | uint16 |  |  | R | M | Include this model for secure metering
Header |  | 1 |  | 1 | L |  | 42 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 4 | 2 | 1 | PhV | Voltage |  | int16 | V | V_SF | R | O | Average phase or line voltage
Fixed Block |  | 5 | 3 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 6 | 4 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 7 | 5 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 8 | 6 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 9 | 7 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 10 | 8 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 11 | 9 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 12 | 10 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 13 | 11 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 14 | 12 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 15 | 13 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 16 | 14 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 18 | 16 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 20 | 18 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 21 | 19 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 23 | 21 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 25 | 23 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 26 | 24 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 28 | 26 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 30 | 28 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 32 | 30 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 34 | 32 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 35 | 33 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
Fixed Block |  | 37 | 35 | Size: 1; Name: Rsrvd; Type: pad; R/W: R | M
Fixed Block |  | 38 | 36 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 40 | 38 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 41 | 39 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 42 | 40 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 43 | 41 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 44 | 0 | Size: 1; Name: DS; Type: uint16; R/W: R | M
bitfield32 | Evt |  |  | Name: Power_Failure; Label: Power Failure; Value: 2 |  | Loss of power or phase
bitfield32 | Evt |  |  | Name: Under_Voltage; Label: Under Voltage; Value: 3 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Name: Low_PF; Label: Low PF; Value: 4 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Name: Over_Current; Label: Over Current; Value: 5 |  | Current Input over threshold
bitfield32 | Evt |  |  | Name: Over_Voltage; Label: Over Voltage; Value: 6 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Name: Missing_Sensor; Label: Missing Sensor; Value: 7 |  | Sensor not connected
bitfield32 | Evt |  |  | Name: OEM01; Label: OEM01; Value: 16 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM02; Label: OEM02; Value: 17 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM03; Label: OEM01; Value: 18 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM04; Label: OEM04; Value: 19 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM05; Label: OEM05; Value: 20 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM06; Label: OEM06; Value: 21 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM07; Label: OEM07; Value: 22 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM08; Label: OEM08; Value: 23 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM09; Label: OEM09; Value: 24 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM10; Label: OEM10; Value: 25 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM11; Label: OEM11; Value: 26 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM12; Label: OEM12; Value: 27 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM13; Label: OEM13; Value: 28 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM14; Label: OEM14; Value: 29 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM15; Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 302
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Irradiance Model | 302 | uint16 |  |  | R | M | Include to support various irradiance measurements
Header |  | 1 |  | 1 | L |  | 5 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irradiance
Fixed Block |  | 3 | 1 | 1 | POAI | POAI |  | uint16 | W/m2 |  | R | O | Plane-of-Array Irradiance
Fixed Block |  | 4 | 2 | 1 | DFI | DFI |  | uint16 | W/m2 |  | R | O | Diffuse Irradiance
Fixed Block |  | 5 | 3 | 1 | DNI | DNI |  | uint16 | W/m2 |  | R | O | Direct Normal Irradiance
Fixed Block |  | 6 | 4 | 1 | OTI | OTI |  | uint16 | W/m2 |  | R | O | Other Irradiance

## 303
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Back of Module Temperature Model | 303 | uint16 |  |  | R | M | Include to support variable number of back of module temperature measurements
Header |  | 1 |  | 1 | L |  | (RB Count * 1) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | 1 | TmpBOM | Temp |  | int16 | C | -1 | R | M | Back of module temperature measurement

## 304
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inclinometer Model | 304 | uint16 |  |  | R | M | Include to support orienation measurements
Header |  | 1 |  | 1 | L |  | (RB Count * 6) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | 2 | Inclx | X |  | int32 | Degrees | -2 | R | M | X-Axis inclination
Repeating Block |  | 4 | 2 | 2 | Incly | Y |  | int32 | Degrees | -2 | R | O | Y-Axis inclination
Repeating Block |  | 6 | 4 | 2 | Inclz | Z |  | int32 | Degrees | -2 | R | O | Z-Axis inclination

## 305
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | GPS | 305 | uint16 |  |  | R | M | Include to support location measurements
Header |  | 1 |  | 1 | L |  | 36 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 6 | Tm | Tm |  | string | hhmmss.sssZ |  | R | O | UTC 24 hour time stamp to millisecond hhmmss.sssZ format
Fixed Block |  | 8 | 6 | 4 | Date | Date |  | string | YYYYMMDD |  | R | O | UTC Date string YYYYMMDD format
Fixed Block |  | 12 | 10 | 20 | Loc | Location |  | string | text |  | R | O | Location string (40 chars max)
Fixed Block |  | 32 | 30 | 2 | Lat | Lat |  | int32 | Degrees | -7 | R | O | Lattitude with seven degrees of precision
Fixed Block |  | 34 | 32 | 2 | Long | Long |  | int32 | Degrees | -7 | R | O | Longitude with seven degrees of precision
Fixed Block |  | 36 | 34 | 2 | Alt | Altitude |  | int32 | meters |  | R | O | Altitude measurement in meters

## 306
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Reference Point Model | 306 | uint16 |  |  | R | M | Include to support a standard reference point
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irrandiance
Fixed Block |  | 3 | 1 | 1 | A | Amps |  | uint16 | W/m2 |  | R | O | Current measurment at reference point
Fixed Block |  | 4 | 2 | 1 | V | Voltage |  | uint16 | W/m2 |  | R | O | Voltage measurment at reference point
Fixed Block |  | 5 | 3 | 1 | Tmp | Temperature |  | uint16 | W/m2 |  | R | O | Temperature measurment at reference point

## 307
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Base Met | 307 | uint16 |  |  | R | M | Base Meteorolgical Model | This model supersedes model 301
Header |  | 1 |  | 1 | L |  | 11 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | TmpAmb | Ambient Temperature |  | int16 | C | -1 | R | O
Fixed Block |  | 3 | 1 | 1 | RH | Relative Humidity |  | int16 | Pct |  | R | O
Fixed Block |  | 4 | 2 | 1 | Pres | Barometric Pressure |  | int16 | HPa |  | R | O
Fixed Block |  | 5 | 3 | 1 | WndSpd | Wind Speed |  | int16 | mps |  | R | O
Fixed Block |  | 6 | 4 | 1 | WndDir | Wind Direction |  | int16 | deg |  | R | O
Fixed Block |  | 7 | 5 | 1 | Rain | Rainfall |  | int16 | mm |  | R | O
Fixed Block |  | 8 | 6 | 1 | Snw | Snow Depth |  | int16 | mm |  | R | O
Fixed Block |  | 9 | 7 | 1 | PPT | Precipitation Type |  | int16 |  |  | R | O | Precipitation Type (WMO 4680 SYNOP code reference)
Fixed Block |  | 10 | 8 | 1 | ElecFld | Electric Field |  | int16 | Vm |  | R | O
Fixed Block |  | 11 | 9 | 1 | SurWet | Surface Wetness |  | int16 | kO |  | R | O
Fixed Block |  | 12 | 10 | 1 | SoilWet | Soil Wetness |  | int16 | Pct |  | R | O

## 308
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Mini Met Model | 308 | uint16 |  |  | R | M | Include to support a few basic measurements
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irradiance
Fixed Block |  | 3 | 1 | 1 | TmpBOM | Temp |  | int16 | C | -1 | R | O | Back of module temperature measurement
Fixed Block |  | 4 | 2 | 1 | TmpAmb | Ambient Temperature |  | int16 | C | -1 | R | O
Fixed Block |  | 5 | 3 | 1 | WndSpd | Wind Speed |  | uint16 | m/s |  | R | O

## 401
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Current) | 401 | uint16 |  |  | R | M | A basic string combiner | This model is SUPERSEDED by model 403
Header |  | 1 |  | 1 | L |  | 14 + (RB Count * 8) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 6 | 4 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 7 | 5 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 11 | 9 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 12 | 10 | 2 | DCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 14 | 12 | 1 | DCV | Voltage |  | uint16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 15 | 13 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Repeating Block |  | 16 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 17 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 19 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 21 | 5 | 1 | InDCA | Amps |  | int16 | A | DCA_SF | R | M | String Input Current
Repeating Block |  | 22 | 6 | 2 | InDCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | String Input Amp-Hours
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 402
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Advanced) | 402 | uint16 |  |  | R | M | An advanced string combiner | This model is SUPERSEDED by model 404
Header |  | 1 |  | 1 | L |  | 20 + (RB Count * 14) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 6 | 4 | Size: 1; Name: DCWh_SF; Type: sunssf; R/W: R | M | Energy scale factor
Fixed Block |  | 7 | 5 | 1 | DCAMax | Rating |  | uint16 | A |  | R | O | Maximum DC Current Rating
Fixed Block |  | 8 | 6 | 1 | N | N |  | count |  |  | R | O | Number of Inputs
Fixed Block |  | 9 | 7 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 11 | 9 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 13 | 11 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 14 | 12 | 2 | DCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 16 | 14 | 1 | DCV | Voltage |  | uint16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 17 | 15 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 18 | 16 | 1 | DCW | Watts |  | int16 | W | DCW_SF | R | O | Output power
Fixed Block |  | 19 | 17 | 1 | DCPR | PR |  | uint16 | Pct |  | R | O | DC Performance ratio value
Fixed Block |  | 20 | 18 | 2 | DCWh | Watt-hours |  | uint32 | Wh | DCWh_SF | R | M | Output energy
Repeating Block |  | 22 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 23 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 25 | 3 | Size: 2; Name: EvtVnd; Type: bitfield32; R/W: R | O
Repeating Block |  | 27 | 5 | 1 | InDCA | Amps |  | int16 | A | DCA_SF | R | M | String Input Current
Repeating Block |  | 28 | 6 | 2 | InDCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | String Input Amp-Hours
Repeating Block |  | 30 | 8 | 1 | InDCV | Voltage |  | uint16 | V | DCV_SF | R | O | String Input Voltage
Repeating Block |  | 31 | 9 | 1 | InDCW | Watts |  | int16 | W | DCWh_SF | R | O | String Input Power
Repeating Block |  | 32 | 10 | 2 | InDCWh | Watt-hours |  | uint32 | Wh |  | R | O | String Input Energy
Repeating Block |  | 34 | 12 | 1 | InDCPR | PR |  | uint16 | Pct |  | R | O | String Performance Ratio
Repeating Block |  | 35 | 13 | 1 | InN | N |  | uint16 |  |  | R | O | Number of modules in this input string | Configured value
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 403
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Current) | 403 | uint16 |  |  | R | M | A basic string combiner model | This model supersedes model 401
Header |  | 1 |  | 1 | L |  | 16 + (RB Count * 8) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 6 | 4 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 7 | 5 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 11 | 9 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 12 | 10 | 2 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 14 | 12 | 1 | DCV | Voltage |  | int16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 15 | 13 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 16 | 14 | Size: 1; Name: InDCA_SF; Type: sunssf; R/W: R | O | Current scale factor for inputs
Fixed Block |  | 17 | 15 | Size: 1; Name: InDCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor for inputs
Repeating Block |  | 18 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 19 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 21 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 23 | 5 | 1 | InDCA | Amps |  | int16 | A | InDCA_SF | R | M | String Input Current
Repeating Block |  | 24 | 6 | 2 | InDCAhr | Amp-hours |  | acc32 | Ah | InDCAhr_SF | R | O | String Input Amp-Hours
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 404
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Advanced) | 404 | uint16 |  |  | R | M | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
Header |  | 1 |  | 1 | L |  | 25 + (RB Count * 14) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 6 | 4 | Size: 1; Name: DCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor
Fixed Block |  | 7 | 5 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 8 | 6 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 9 | 7 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 11 | 9 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 13 | 11 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 14 | 12 | 2 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 16 | 14 | 1 | DCV | Voltage |  | int16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 17 | 15 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 18 | 16 | 1 | DCW | Watts |  | int16 | W | DCW_SF | R | O | Output power
Fixed Block |  | 19 | 17 | 1 | DCPR | PR |  | int16 | Pct |  | R | O | DC Performance ratio value
Fixed Block |  | 20 | 18 | 2 | DCWh | Watt-hours |  | acc32 | Wh | DCWh_SF | R | O | Output energy
Fixed Block |  | 22 | 20 | Size: 1; Name: InDCA_SF; Type: sunssf; R/W: R | O | Current scale factor for inputs
Fixed Block |  | 23 | 21 | Size: 1; Name: InDCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor for inputs
Fixed Block |  | 24 | 22 | Size: 1; Name: InDCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor for inputs
Fixed Block |  | 25 | 23 | Size: 1; Name: InDCW_SF; Type: sunssf; R/W: R | O | Power scale factor for inputs
Fixed Block |  | 26 | 24 | Size: 1; Name: InDCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor for inputs
Repeating Block |  | 27 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 28 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 30 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 32 | 5 | 1 | InDCA | Amps |  | int16 | A | InDCA_SF | R | M | String Input Current
Repeating Block |  | 33 | 6 | 2 | InDCAhr | Amp-hours |  | acc32 | Ah | InDCAhr_SF | R | O | String Input Amp-Hours
Repeating Block |  | 35 | 8 | 1 | InDCV | Voltage |  | int16 | V | InDCV_SF | R | O | String Input Voltage
Repeating Block |  | 36 | 9 | 1 | InDCW | Watts |  | int16 | W | InDCW_SF | R | O | String Input Power
Repeating Block |  | 37 | 10 | 2 | InDCWh | Watt-hours |  | acc32 | Wh | InDCWh_SF | R | O | String Input Energy
Repeating Block |  | 39 | 12 | 1 | InDCPR | PR |  | uint16 | Pct |  | R | O | String Performance Ratio
Repeating Block |  | 40 | 13 | 1 | InN | N |  | uint16 |  |  | R | O | Number of modules in this input string | Configured value
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 501
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Solar Module | 501 | uint16 |  |  | R | M | A solar module model supporing DC-DC converter | Float
Header |  | 1 |  | 1 | L |  | 31 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Stat | Status |  | enum16 |  |  | R | M | Enumerated value. Module Status Code
Fixed Block |  | 3 | 1 | 1 | StatVend | Vendor Status |  | enum16 |  |  | R | O | Module Vendor Status Code
Fixed Block |  | 4 | 2 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Bitmask value. Module Event Flags
Fixed Block |  | 6 | 4 | 2 | EvtVend | Vendor Module Event Flags |  | bitfield32 |  |  | R | O | Vendor specific flags
Fixed Block |  | 8 | 6 | 1 | Ctl | Control |  | enum16 |  |  | RW | O | Module Control
Fixed Block |  | 9 | 7 | 2 | CtlVend | Vendor Control |  | enum32 |  |  | RW | O | Vendor Module Control
Fixed Block |  | 11 | 9 | 2 | CtlVal | Control Value |  | int32 |  |  | RW | O | Module Control Value
Fixed Block |  | 13 | 11 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O | Time in seconds since 2000 epoch
Fixed Block |  | 15 | 13 | 2 | OutA | Output Current |  | float32 | A |  | R | O | Output Current
Fixed Block |  | 17 | 15 | 2 | OutV | Output Voltage |  | float32 | V |  | R | O | Output Voltage
Fixed Block |  | 19 | 17 | 2 | OutWh | Output Energy |  | float32 | Wh |  | R | O | Output Energy
Fixed Block |  | 21 | 19 | 2 | OutW | Output Power |  | float32 | W |  | R | O | Output Power
Fixed Block |  | 23 | 21 | 2 | Tmp | Temp |  | float32 | C |  | R | O | Module Temperature
Fixed Block |  | 25 | 23 | 2 | InA | Input Current |  | float32 | A |  | R | O | Input Current
Fixed Block |  | 27 | 25 | 2 | InV | Input Voltage |  | float32 | V |  | R | O | Input Voltage
Fixed Block |  | 29 | 27 | 2 | InWh | Input Energy |  | float32 | Wh |  | R | O | Input Energy
Fixed Block |  | 31 | 29 | 2 | InW | Input Power |  | float32 | W |  | R | O | Input Power
enum16 | Stat |  |  | Name: OFF; Label: Off; Value: 1 |  | Module is in the OFF state
enum16 | Stat |  |  | Name: SLEEPING; Label: SLEEPING; Value: 2 |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
enum16 | Stat |  |  | Name: STARTING; Label: STARTING; Value: 3 |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
enum16 | Stat |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Tracking MPPT power point
enum16 | Stat |  |  | Name: THROTTLED; Label: THROTTLED; Value: 5 |  | Forced power reduction / power de-rating
enum16 | Stat |  |  | Name: SHUTTING_DOWN; Label: SHUTTING_DOWN; Value: 6 |  | Shutting down
enum16 | Stat |  |  | Name: FAULT; Label: FAULT; Value: 7 |  | One or more faults exist
enum16 | Stat |  |  | Name: STANDBY; Label: STANDBY; Value: 8 |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
enum16 | Stat |  |  | Name: TEST; Label: TEST; Value: 9 |  | Test mode
enum16 | Stat |  |  | Name: OTHER; Label: OTHER; Value: 10 |  | As defined in vendor specific status
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0 |  | Ground Fault
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Over Voltage; Value: 1 |  | DC input over-voltage
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 11 |  | Reserved | Reserved for u-inverter compatibility
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: Disconnect; Value: 3 |  | DC disconnect open
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6 |  | Manual shutdown
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Label: Over Temperature; Value: 7 |  | Over Temperature
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12 |  | Input fuse is blown
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Label: Under Temperature; Value: 13 |  | Under Temperature
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14 |  | Generic Memory or Communication Error
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15 |  | Arc Detection
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Label: Theft Detection; Value: 16 |  | Theft Detection
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Label: Over Current; Value: 17 |  | Output Over Current
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Label: Output Over Voltage; Value: 18 |  | DC Output Over Voltage
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Label: Output Under Voltage; Value: 19 |  | DC Output Under Voltage
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20 |  | Last Self Test failed; see vendor event for details

## 502
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Solar Module | 502 | uint16 |  |  | R | M | A solar module model supporing DC-DC converter | Integer
Header |  | 1 |  | 1 | L |  | 28 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | O | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: Wh_SF; Type: sunssf; R/W: R | O | Energy scale factor
Fixed Block |  | 6 | 4 | 1 | Stat | Status |  | enum16 |  |  | R | M | Enumerated value. Module Status Code
Fixed Block |  | 7 | 5 | 1 | StatVend | Vendor Status |  | enum16 |  |  | R | O | Module Vendor Status Code
Fixed Block |  | 8 | 6 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Bitmask value. Module Event Flags
Fixed Block |  | 10 | 8 | 2 | EvtVend | Vendor Module Event Flags |  | bitfield32 |  |  | R | O | Vendor specific flags
Fixed Block |  | 12 | 10 | 1 | Ctl | Control |  | enum16 |  |  | RW | O | Module Control
Fixed Block |  | 13 | 11 | 2 | CtlVend | Vendor Control |  | enum32 |  |  | RW | O | Vendor Module Control
Fixed Block |  | 15 | 13 | 2 | CtlVal | Control Value |  | int32 |  |  | RW | O | Module Control Value
Fixed Block |  | 17 | 15 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O | Time in seconds since 2000 epoch
Fixed Block |  | 19 | 17 | 1 | OutA | Output Current |  | int16 | A | A_SF | R | O | Output Current
Fixed Block |  | 20 | 18 | 1 | OutV | Output Voltage |  | int16 | V | V_SF | R | O | Output Voltage
Fixed Block |  | 21 | 19 | 2 | OutWh | Output Energy |  | acc32 | Wh | Wh_SF | R | O | Output Energy
Fixed Block |  | 23 | 21 | 1 | OutPw |  |  | int16 | W | W_SF | R | O
Fixed Block |  | 24 | 22 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Module Temperature
Fixed Block |  | 25 | 23 | 1 | InA | Input Current |  | int16 | A | A_SF | R | O | Input Current
Fixed Block |  | 26 | 24 | 1 | InV | Input Voltage |  | int16 | V | V_SF | R | O | Input Voltage
Fixed Block |  | 27 | 25 | 2 | InWh | Input Energy |  | acc32 | Wh | Wh_SF | R | O | Input Energy
Fixed Block |  | 29 | 27 | 1 | InW | Input Power |  | int16 | W | W_SF | R | O | Input Power
enum16 | Stat |  |  | Name: OFF; Label: Off; Value: 1 |  | Module is in the OFF state
enum16 | Stat |  |  | Name: SLEEPING; Label: SLEEPING; Value: 2 |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
enum16 | Stat |  |  | Name: STARTING; Label: STARTING; Value: 3 |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
enum16 | Stat |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Tracking MPPT power point
enum16 | Stat |  |  | Name: THROTTLED; Label: THROTTLED; Value: 5 |  | Forced power reduction / power de-rating
enum16 | Stat |  |  | Name: SHUTTING_DOWN; Label: SHUTTING_DOWN; Value: 6 |  | Shutting down
enum16 | Stat |  |  | Name: FAULT; Label: FAULT; Value: 7 |  | One or more faults exist
enum16 | Stat |  |  | Name: STANDBY; Label: STANDBY; Value: 8 |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
enum16 | Stat |  |  | Name: TEST; Label: TEST; Value: 9 |  | Test mode
enum16 | Stat |  |  | Name: OTHER; Label: OTHER; Value: 10 |  | As defined in vendor specific status
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0 |  | Ground Fault
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Over Voltage; Value: 1 |  | DC input over-voltage
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 11 |  | Reserved | Reserved for u-inverter compatibility
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: Disconnect; Value: 3 |  | DC disconnect open
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6 |  | Manual shutdown
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Label: Over Temperature; Value: 7 |  | Over Temperature
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12 |  | Input fuse is blown
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Label: Under Temperature; Value: 13 |  | Under Temperature
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14 |  | Generic Memory or Communication Error
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15 |  | Arc Detection
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Label: Theft Detection; Value: 16 |  | Theft Detection
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Label: Over Current; Value: 17 |  | Output Over Current
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Label: Output Over Voltage; Value: 18 |  | DC Output Over Voltage
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Label: Output Under Voltage; Value: 19 |  | DC Output Under Voltage
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20 |  | Last Self Test failed; see vendor event for details

## 601
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Tracker Controller DRAFT 2 | 601 | uint16 |  |  | R | M | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
Header |  | 1 |  | 1 | L |  | 26 + (RB Count * 22) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 8 | Nam | Controller |  | string |  |  | R | O | Descriptive name for this control unit
Fixed Block |  | 10 | 8 | 1 | Typ | Type |  | enum16 |  |  | R | M | Type of tracker
Fixed Block |  | 11 | 9 | 5 | DtLoc | Date |  | string | YYYYMMDD |  | R | O | Local date in YYYYMMDD format
Fixed Block |  | 16 | 14 | 3 | TmLoc | Time |  | string | hhmmss |  | R | O | 24 hour local time stamp to second
Fixed Block |  | 19 | 17 | 1 | Day | Day |  | uint16 |  |  | R | O | Number of the day in the year (1-366)
Fixed Block |  | 20 | 18 | 2 | GlblElCtl | Manual Elevation |  | int32 | Degrees | Dgr_SF | RW | O | Global manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type
Fixed Block |  | 22 | 20 | 2 | GlblAzCtl | Manual Azimuth |  | int32 | Degrees | Dgr_SF | RW | O | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
Fixed Block |  | 24 | 22 | 1 | GlblCtl | Mode |  | enum16 |  |  | RW | O | Global Control register operates on all trackers. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete. | The global controls all trackers
Fixed Block |  | 25 | 23 | 1 | GlblAlm | Alarm |  | bitfield16 |  |  | R | O | Global tracker alarm conditions | Combined tracker alarm conditions. See individual trackers for alarms
Fixed Block |  | 26 | 24 | 1 | Dgr_SF | SF |  | sunssf |  |  | R | M | Scale Factor for targets and position measurements in degrees
Fixed Block |  | 27 | 25 | 1 | N | Trackers |  | uint16 |  |  | R | M | Number of trackers being controlled. Size of repeating block.
Repeating Block |  | 28 | 0 | 8 | Id | Tracker |  | string |  |  | R | O | Descriptive name for this tracker unit
Repeating Block |  | 36 | 8 | 2 | ElTrgt | Target Elevation |  | int32 | Degrees | Dgr_SF | R | O | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 38 | 10 | 2 | AzTrgt | Target Azimuth |  | int32 | Degrees | SF | R | O | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 40 | 12 | 2 | ElPos | Elevation |  | int32 | Degrees | Dgr_SF | R | O | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 42 | 14 | 2 | AzPos | Azimuth |  | int32 | Degrees | Dgr_SF | R | O | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 44 | 16 | 2 | ElCtl | Manual Elevation |  | int32 | Degrees | Dgr_SF | RW | O | Manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type
Repeating Block |  | 46 | 18 | 2 | AzCtl | Manual Azimuth |  | int32 | Degrees | Dgr_SF | RW | O | Manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
Repeating Block |  | 48 | 20 | 1 | Ctl | Mode |  | enum16 |  |  | RW | O | Control register. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
Repeating Block |  | 49 | 21 | 1 | Alm | Alarm |  | bitfield16 |  |  | R | O | Tracker alarm conditions
enum16 | Typ |  |  | Name: Unknown; Label: Unknown; Value: 0 |  | Not Set
enum16 | Typ |  |  | Name: Fixed; Label: Fixed; Value: 1 |  | Documented orientation information
enum16 | Typ |  |  | Name: Horizontal; Label: Horizontal; Value: 2 |  | Single Axis Horizontal
enum16 | Typ |  |  | Name: Tilted; Label: Tilted; Value: 3 |  | Single Axis Tilted Horizontal
enum16 | Typ |  |  | Name: Azimuth; Label: Azimuth; Value: 4 |  | Single Axis Azimuth
enum16 | Typ |  |  | Name: Dual; Label: Dual; Value: 5 |  | Dual Axis
enum16 | Typ |  |  | Name: Other; Label: Other; Value: 99 |  | Other type
enum16 | GlblCtl |  |  | Name: Automatic; Label: Auto; Value: 0 |  | Follow programmed path
enum16 | GlblCtl |  |  | Name: Manual; Label: Manual; Value: 1 |  | Go to a fixed position
enum16 | GlblCtl |  |  | Name: Calibrate; Label: Calibrate; Value: 2 |  | Execute test mode
bitfield16 | GlblAlm |  |  | Name: SetPoint; Label: SetPoint; Value: 0 |  | One or more trackers are NOT at SetPoint
bitfield16 | GlblAlm |  |  | Name: ObsEl; Label: ObsEl; Value: 1 |  | One or more trackers ELEVATION motor is obstructed
bitfield16 | GlblAlm |  |  | Name: ObsAz; Label: ObsAz; Value: 2 |  | One or more trackers AZIMUTH motor is obstructed
enum16 | Ctl |  |  | Name: Automatic; Label: Auto; Value: 0 |  | Follow programmed path
enum16 | Ctl |  |  | Name: Manual; Label: Manual; Value: 1 |  | Go to a fixed position
enum16 | Ctl |  |  | Name: Calibrate; Label: Calibrate; Value: 2 |  | Execute test mode
bitfield16 | Alm |  |  | Name: SetPoint; Label: SetPoint; Value: 0 |  | One or more trackers are NOT at SetPoint
bitfield16 | Alm |  |  | Name: ObsEl; Label: ObsEl; Value: 1 |  | One or more trackers ELEVATION motor is obstructed
bitfield16 | Alm |  |  | Name: ObsAz; Label: ObsAz; Value: 2 |  | One or more trackers AZIMUTH motor is obstructed

## 801
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Energy Storage Base Model (DEPRECATED) | 801 | uint16 |  |  | R | M | This model has been deprecated.
Header |  | 1 |  | 1 | L |  | 1 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DEPRECATED | Deprecated Model |  | enum16 |  |  | R | M | This model has been deprecated.

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 62 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AHRtg | Nameplate Charge Capacity |  | uint16 | Ah | AHRtg_SF | R | M | Nameplate charge capacity in amp-hours.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WChaRteMax | Nameplate Max Charge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer into the storage device in DC watts.
Fixed Block |  | 5 | 3 | 1 | WDisChaRteMax | Namplate Max Discharge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer out of the storage device in DC watts.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCMax | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCMin | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | SocRsvMax | Max Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | SoCRsvMin | Min Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 12 | 10 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth of discharge, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 14 | 12 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 16 | 14 | 1 | ChaSt | Charge Status |  | enum16 |  |  | R | O | Charge status of storage device. Enumeration.
Fixed Block |  | 17 | 15 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | Battery control mode. Enumeration. | Maps to DRCC.LocRemCtl in IEC 61850.
Fixed Block |  | 18 | 16 | 1 | Hb | Battery Heartbeat |  | uint16 |  |  | R | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 19 | 17 | 1 | CtrlHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 20 | 18 | 1 | AlmRst | Alarm Reset |  | uint16 |  |  | RW | M | Used to reset any latched alarms. 1 = Reset. | Battery should reset to 0 when reset is complete.
Fixed Block |  | 21 | 19 | 1 | Typ | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT.BatTyp in 61850.
Fixed Block |  | 22 | 20 | 1 | State | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with State in IEC 61850.
Fixed Block |  | 23 | 21 | 1 | StateVnd | Vendor Battery Bank State |  | enum16 |  |  | R | O | Vendor specific battery bank state. Enumeration.
Fixed Block |  | 24 | 22 | 2 | WarrDt | Warranty Date |  | uint32 |  |  | R | O | Date the device warranty expires. | Number of days since 1/1/2000.
Fixed Block |  | 26 | 24 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 28 | 26 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 30 | 28 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 32 | 30 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 34 | 32 | 1 | V | External Battery Voltage |  | uint16 | V | V_SF | R | M | DC Bus Voltage. | Maps to ZBAT.V in IEC 61850.
Fixed Block |  | 35 | 33 | 1 | VMax | Max Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous maximum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 36 | 34 | 1 | VMin | Min Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous minimum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 37 | 35 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 38 | 36 | 1 | CellVMaxStr | Max Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with maximum voltage.
Fixed Block |  | 39 | 37 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum voltage.
Fixed Block |  | 40 | 38 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 41 | 39 | 1 | CellVMinStr | Min Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with minimum voltage.
Fixed Block |  | 42 | 40 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum voltage.
Fixed Block |  | 43 | 41 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average cell voltage for all cells in the bank. | Calculation based on measurements.
Fixed Block |  | 44 | 42 | 1 | A | Total DC Current |  | int16 | A | A_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement.
Fixed Block |  | 45 | 43 | 1 | AChaMax | Max Charge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC charge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
Fixed Block |  | 46 | 44 | 1 | ADisChaMax | Max Discharge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC discharge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
Fixed Block |  | 47 | 45 | 1 | W | Total Power |  | int16 | W | W_SF | R | M | Total power flowing to/from the battery bank. | Measurement.
Fixed Block |  | 48 | 46 | 1 | ReqInvState | Inverter State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the inverter. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 49 | 47 | 1 | ReqW | Battery Power Request |  | int16 | W | W_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 50 | 48 | 1 | SetOp | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 51 | 49 | 1 | SetInvState | Set Inverter State |  | enum16 |  |  | RW | M | Set the current state of the inverter. | Information needed by battery for some operations.
Fixed Block |  | 52 | 50 | Size: 1; Name: AHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for charge capacity.
Fixed Block |  | 53 | 51 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 54 | 52 | Size: 1; Name: WChaDisChaMax_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 55 | 53 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 56 | 54 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 57 | 55 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for depth of discharge.
Fixed Block |  | 58 | 56 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for state of health.
Fixed Block |  | 59 | 57 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for DC bus voltage.
Fixed Block |  | 60 | 58 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 61 | 59 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for DC current.
Fixed Block |  | 62 | 60 | Size: 1; Name: AMax_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 63 | 61 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 0 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in IEC 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 1 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in IEC 61850.
enum16 | Typ |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | Typ |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | Typ |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | Typ |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | Typ |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | Typ |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | Typ |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | Typ |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | Typ |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | Typ |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | Typ |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | Typ |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | State |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | State |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | State |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | State |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | State |  |  | Name: SOC PROTECTION; Label: SoC Protection; Value: 5 |  | Battery bank is connected but SoC is too low. Battery should be considered "offline".
enum16 | State |  |  | Name: SUSPENDING; Label: Suspending; Value: 6 |  | Battery bank is suspending operation and will disconnect.
enum16 | State |  |  | Name: FAULT; Label: Fault; Value: 99 |  | The battery has experienced a critical failure and may not be operated.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery maximum charge current. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery maximum discharge current has been exceeded. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery state of charge has reached or exceeded SoCMin
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery state of charge is approaching SoCMin
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery state of charge has reached or exceeded SoCMax
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery state of charge is approaching SoCMax
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 24 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery bank has been configured incorrectly and will not operate.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery bank has been configured incorrectly and may not operated as expected.
enum16 | ReqInvState |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the inverter.
enum16 | ReqInvState |  |  | Name: START; Label: Start Inverter; Value: 1 |  | Battery requests that the inverter be started. | Battery is notified of inverter state change through SetInvState.
enum16 | ReqInvState |  |  | Name: STOP; Label: Stop Inverter; Value: 2 |  | Battery requests that the inverter be stopped. | Battery is notified of inverter state change through SetInvState.
enum16 | SetOp |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | SetOp |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | SetInvState |  |  | Name: INVERTER_STOPPED; Label: Inverter is Stopped; Value: 1
enum16 | SetInvState |  |  | Name: INVERTER_STANDBY; Label: Inverter is in Standby; Value: 2
enum16 | SetInvState |  |  | Name: INVERTER_STARTED; Label: Inverter is Started; Value: 3

## 803
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Battery Bank Model | 803 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 26 + (RB Count * 32) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | NStr | String Count |  | uint16 |  |  | R | M | Number of strings in the bank.
Fixed Block |  | 3 | 1 | 1 | NStrCon | Connected String Count |  | uint16 |  |  | R | M | Number of strings with contactor closed.
Fixed Block |  | 4 | 2 | 1 | ModTmpMax | Max Module Temperature |  | int16 |  | ModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement.
Fixed Block |  | 5 | 3 | 1 | ModTmpMaxStr | Max Module Temperature String |  | uint16 |  |  | R | O | String containing the module with maximum temperature.
Fixed Block |  | 6 | 4 | 1 | ModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | O | Module with maximum temperature.
Fixed Block |  | 7 | 5 | 1 | ModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement.
Fixed Block |  | 8 | 6 | 1 | ModTmpMinStr | Min Module Temperature String |  | uint16 |  |  | R | O | String containing the module with minimum temperature.
Fixed Block |  | 9 | 7 | 1 | ModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | O | Module with minimum temperature.
Fixed Block |  | 10 | 8 | 1 | ModTmpAvg | Average Module Temperature |  | uint16 |  |  | R | O | Average temperature for all modules in the bank. | Calculation based on measurements.
Fixed Block |  | 11 | 9 | 1 | StrVMax | Max String Voltage |  | uint16 | V | V_SF | R | O | Maximum string voltage for all strings in the bank. | Measurement.
Fixed Block |  | 12 | 10 | 1 | StrVMaxStr | Max String Voltage String |  | uint16 |  |  | R | O | String with maximum voltage.
Fixed Block |  | 13 | 11 | 1 | StrVMin | Min String Voltage |  | uint16 | V | V_SF | R | O | Minimum string voltage for all strings in the bank. | Measurement.
Fixed Block |  | 14 | 12 | 1 | StrVMinStr | Min String Voltage String |  | uint16 |  |  | R | O | String with minimum voltage.
Fixed Block |  | 15 | 13 | 1 | StrVAvg | Average String Voltage |  | uint16 | V | V_SF | R | O | Average string voltage for all strings in the bank. | Calculation based on measurements.
Fixed Block |  | 16 | 14 | 1 | StrAMax | Max String Current |  | int16 | A | A_SF | R | O | Maximum current of any string in the bank. | Measurement.
Fixed Block |  | 17 | 15 | 1 | StrAMaxStr | Max String Current String |  | uint16 |  |  | R | O | String with the maximum current.
Fixed Block |  | 18 | 16 | 1 | StrAMin | Min String Current |  | int16 | A | A_SF | R | O | Minimm current of any string in the bank. | Measurement.
Fixed Block |  | 19 | 17 | 1 | StrAMinStr | Min String Current String |  | uint16 |  |  | R | O | String with the minimum current.
Fixed Block |  | 20 | 18 | 1 | StrAAvg | Average String Current |  | int16 | A | A_SF | R | O | Average string current for all strings in the bank. | Calculation based on measurements.
Fixed Block |  | 21 | 19 | 1 | NCellBal | Battery Cell Balancing Count |  | uint16 |  |  | R | O | Total number of cells that are currently being balanced.
Fixed Block |  | 22 | 20 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 23 | 21 | Size: 1; Name: ModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperatures.
Fixed Block |  | 24 | 22 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for string currents.
Fixed Block |  | 25 | 23 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for string state of health.
Fixed Block |  | 26 | 24 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for string state of charge.
Fixed Block |  | 27 | 25 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Scale factor for string voltage.
Repeating Block |  | 28 | 0 | 1 | StrNMod | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Repeating Block |  | 29 | 1 | 2 | StrSt | String Status |  | bitfield32 |  |  | R | M | Current status of the string.
Repeating Block |  | 31 | 3 | 1 | StrConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 32 | 4 | 1 | StrSoC | String State of Charge |  | uint16 | % | SoC_SF | R | M | Battery string state of charge, expressed as a percentage. | Measurement.
Repeating Block |  | 33 | 5 | 1 | StrSoH | String State of Health |  | uint16 | % | SoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement.
Repeating Block |  | 34 | 6 | 1 | StrA | String Current |  | int16 | A | A_SF | R | M | String current measurement. | Measurement.
Repeating Block |  | 35 | 7 | 1 | StrCellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the string. | Measurement.
Repeating Block |  | 36 | 8 | 1 | StrCellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the maximum cell voltage.
Repeating Block |  | 37 | 9 | 1 | StrCellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the string. | Measurement.
Repeating Block |  | 38 | 10 | 1 | StrCellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the minimum cell voltage.
Repeating Block |  | 39 | 11 | 1 | StrCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the string. | Calculation based on measurements.
Repeating Block |  | 40 | 12 | 1 | StrModTmpMax | Max Module Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement.
Repeating Block |  | 41 | 13 | 1 | StrModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | O | Module with the maximum temperature.
Repeating Block |  | 42 | 14 | 1 | StrModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement.
Repeating Block |  | 43 | 15 | 1 | StrModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | O | Module with the miniumum temperature.
Repeating Block |  | 44 | 16 | 1 | StrModTmpAvg | Average Module Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all modules in the bank. | Calculation based on measurements.
Repeating Block |  | 45 | 17 | 1 | StrDisRsn | Disabled Reason |  | enum16 |  |  | R | O | Reason why the string is currently disabled.
Repeating Block |  | 46 | 18 | 2 | StrConSt | Contactor Status |  | bitfield32 |  |  | R | O | Status of the contactor(s) for the string.
Repeating Block |  | 48 | 20 | 2 | StrEvt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 50 | 22 | 2 | StrEvt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Repeating Block |  | 52 | 24 | 2 | StrEvtVnd1 | Vendor String Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events.
Repeating Block |  | 54 | 26 | 2 | StrEvtVnd2 | Vendor String Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events.
Repeating Block |  | 56 | 28 | 1 | StrSetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. | Should reset to 0 upon completion.
Repeating Block |  | 57 | 29 | 1 | StrSetCon | Connect/Disconnect String |  | enum16 |  |  | RW | O | Connects and disconnects the string. | Should reset to 0 upon completion.
Repeating Block |  | 58 | 30 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 59 | 31 | 1 | Pad2 | Pad |  | pad |  |  | R | M | Pad register.
bitfield32 | StrSt |  |  | Name: STRING_ENABLED; Label: String Is Enabled; Value: 0 |  | String is enabled and will connect next time battery is asked to connect.
bitfield32 | StrSt |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | String contactor is closed. | If string has multiple contactors, indicates that all contactors are closed.
enum16 | StrConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | StrConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | StrConFail |  |  | Name: STR_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | StrConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | StrConFail |  |  | Name: STRING_NOT_ENABLED; Label: String Not Enabled; Value: 4 |  | The string is not enabled.
enum16 | StrConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | StrConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | StrConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A failure during precharge occurred.
enum16 | StrConFail |  |  | Name: STRING_FAULT; Label: String Fault; Value: 8 |  | A string fault has occurred. | See StrEvt1 for more information.
enum16 | StrDisRsn |  |  | Name: NONE; Label: No Reason; Value: 0 |  | No reason provided.
enum16 | StrDisRsn |  |  | Name: FAULT; Label: Fault; Value: 1 |  | A fault has occurred which caused the string to be disabled.
enum16 | StrDisRsn |  |  | Name: MAINTENANCE; Label: Maintenance; Value: 2 |  | The string has been disabled for maintenance reasons.
enum16 | StrDisRsn |  |  | Name: EXTERNAL; Label: External; Value: 3 |  | The string has been disabled by an external user or controller.
enum16 | StrDisRsn |  |  | Name: OTHER; Label: Other; Value: 4 |  | The string has been disabled for some other reason.
bitfield32 | StrConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | StrConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | StrConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | StrConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | StrConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | StrConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | StrConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | StrConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | StrConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | StrConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | StrConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | StrConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | StrConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | StrConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | StrConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | StrConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | StrConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | StrConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | StrConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | StrConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | StrConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | StrConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | StrConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | StrConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | StrConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | StrConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | StrConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | StrConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | StrConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | StrConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | StrConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | StrEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | String is unable to communicate with battery modules.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery string is approaching maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery string has exceeded minimum operating temperature
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery string maximum charge current. | See AChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery string maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery string voltage is approaching maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery string state of charge has reached or exceeded SoCMin
bitfield32 | StrEvt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery string state of charge is approaching SoCMin
bitfield32 | StrEvt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery string state of charge has reached or exceeded SoCMax
bitfield32 | StrEvt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery string state of charge is approaching SoCMax
bitfield32 | StrEvt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | StrEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | StrEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | StrEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | StrEvt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | StrEvt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | StrEvt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | StrEvt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | StrEvt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate.
bitfield32 | StrEvt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
enum16 | StrSetEna |  |  | Name: ENABLE_STRING; Label: Enable String; Value: 1 |  | Enable the string.
enum16 | StrSetEna |  |  | Name: DISABLE_STRING; Label: Disable String; Value: 2 |  | Disable the string.
enum16 | StrSetCon |  |  | Name: CONNECT_STRING; Label: Connect String; Value: 1 |  | Connect the string.
enum16 | StrSetCon |  |  | Name: DISCONNECT_STRING; Label: Disconnect String; Value: 2 |  | Disconnect the string.

## 804
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion String Model | 804 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 46 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Idx | String Index |  | uint16 |  |  | R | M | Index of the string within the bank. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Fixed Block |  | 4 | 2 | 2 | St | String Status |  | bitfield32 |  |  | R | M | Current status of the string.
Fixed Block |  | 6 | 4 | 1 | ConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Fixed Block |  | 7 | 5 | 1 | NCellBal | String Cell Balancing Count |  | uint16 |  |  | R | O | Number of cells currently being balanced in the string.
Fixed Block |  | 8 | 6 | 1 | SoC | String State of Charge |  | uint16 | % | SoC_SF | R | M | Battery string state of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 9 | 7 | 1 | DoD | String Depth of Discharge |  | uint16 | % | StrDoC_SF | R | O | Depth of discharge for the string, expressed as a percentage. | Measurement.
Fixed Block |  | 10 | 8 | 2 | NCyc | String Cycle Count |  | uint32 |  |  | R | O | Number of discharge cycles executed upon the string.
Fixed Block |  | 12 | 10 | 1 | SoH | String State of Health |  | uint16 | % | SoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | A | String Current |  | int16 | A | A_SF | R | M | String current measurement. | Measurement.
Fixed Block |  | 14 | 12 | 1 | V | String Voltage |  | uint16 | V | V_SF | R | O | String voltage measurement. | Measurement.
Fixed Block |  | 15 | 13 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the string. | Measurement.
Fixed Block |  | 16 | 14 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum cell voltage.
Fixed Block |  | 17 | 15 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the string. | Measurement.
Fixed Block |  | 18 | 16 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum cell voltage.
Fixed Block |  | 19 | 17 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the string. | Calculation based on measurements.
Fixed Block |  | 20 | 18 | 1 | ModTmpMax | Max Module Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all modules in the string. | Measurement.
Fixed Block |  | 21 | 19 | 1 | ModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | M | Module with the maximum temperature.
Fixed Block |  | 22 | 20 | 1 | ModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the string. | Measurement.
Fixed Block |  | 23 | 21 | 1 | ModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | M | Module with the minimum temperature.
Fixed Block |  | 24 | 22 | 1 | ModTmpAvg | Average Module Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 25 | 23 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 26 | 24 | 2 | ConSt | Contactor Status |  | bitfield32 |  |  | R | O | Status of the contactor(s) for the string.
Fixed Block |  | 28 | 26 | 2 | Evt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 30 | 28 | 2 | Evt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Fixed Block |  | 32 | 30 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 34 | 32 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 36 | 34 | 1 | SetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. Should reset to 0 upon completion.
Fixed Block |  | 37 | 35 | 1 | SetCon | Connect/Disconnect String |  | enum16 |  |  | RW | O | Connects and disconnects the string. | Should reset to 0 upon completion.
Fixed Block |  | 38 | 36 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for string state of charge.
Fixed Block |  | 39 | 37 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for string state of health.
Fixed Block |  | 40 | 38 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for string depth of discharge.
Fixed Block |  | 41 | 39 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for string current.
Fixed Block |  | 42 | 40 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Scale factor for string voltage.
Fixed Block |  | 43 | 41 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 44 | 42 | Size: 1; Name: ModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperature.
Fixed Block |  | 45 | 43 | 1 | Pad2 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 46 | 44 | 1 | Pad3 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 47 | 45 | 1 | Pad4 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 48 | 0 | 1 | ModNCell | Module Cell Count |  | uint16 |  |  | R | M | Count of all cells in the module.
Repeating Block |  | 49 | 1 | 1 | ModSoC | Module SoC |  | uint16 | % | SoC_SF | R | O | Module state of charge, expressed as a percentage.
Repeating Block |  | 50 | 2 | 1 | ModSoH | Module SoH |  | uint16 | % | SoH_SF | R | O | Module state of health, expressed as a percentage.
Repeating Block |  | 51 | 3 | 1 | ModCellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the module. | Measurement.
Repeating Block |  | 52 | 4 | 1 | ModCellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with maximum voltage.
Repeating Block |  | 53 | 5 | 1 | ModCellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the module. | Measurement.
Repeating Block |  | 54 | 6 | 1 | ModCellVMinCell | Min Cell Voltage Cell |  | uint16 | V | CellV_SF | R | O | Cell with minimum voltage.
Repeating Block |  | 55 | 7 | 1 | ModCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 56 | 8 | 1 | ModCellTmpMax | Max Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all cells in the module. | Measurement.
Repeating Block |  | 57 | 9 | 1 | ModCellTmpMaxCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with maximum temperature.
Repeating Block |  | 58 | 10 | 1 | ModCellTmpMin | Min Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all cells in the module. | Measurement.
Repeating Block |  | 59 | 11 | 1 | ModCellTmpMinCell | Min Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with minimum temperature.
Repeating Block |  | 60 | 12 | 1 | ModCellTmpAvg | Average Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 61 | 13 | 1 | Pad5 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 62 | 14 | 1 | Pad6 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 63 | 15 | 1 | Pad7 | Pad |  | pad |  |  | R | M | Pad register.
bitfield32 | St |  |  | Name: STRING_ENABLED; Label: String Is Enabled; Value: 0 |  | String is enabled and will connect next time battery is asked to connect.
bitfield32 | St |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | String contactor is closed. | If string has multiple contactors, indicates that all contactors are closed.
enum16 | ConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | ConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | ConFail |  |  | Name: STR_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | ConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | ConFail |  |  | Name: STRING_NOT_ENABLED; Label: String Not Enabled; Value: 4 |  | The string is not enabled.
enum16 | ConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | ConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | ConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A precharge failure occurred.
enum16 | ConFail |  |  | Name: STRING_FAULT; Label: String Fault; Value: 8 |  | A string fault has occurred. | See Evt1 for more information.
bitfield32 | ConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | ConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | ConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | ConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | ConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | ConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | ConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | ConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | ConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | ConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | ConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | ConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | ConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | ConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | ConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | ConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | ConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | ConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | ConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | ConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | ConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | ConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | ConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | ConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | ConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | ConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | ConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | ConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | ConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | ConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | ConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | String is unable to communicate with battery modules.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery string is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery string has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery string maximum charge current. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery string maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery string voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery string state of charge has reached or exceeded SoCMin.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery string state of charge is approaching SoCMin.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery string state of charge has reached or exceeded SoCMax.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery string state of charge is approaching SoCMax.
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate as expected.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
enum16 | SetCon |  |  | Name: CONNECT_STRING; Label: Connect String; Value: 1 |  | Connect the string.
enum16 | SetCon |  |  | Name: DISCONNECT_STRING; Label: Disconnect String; Value: 2 |  | Disconnect the string.

## 805
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Module Model | 805 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 42 + (RB Count * 4) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | StrIdx | String Index |  | uint16 |  |  | R | M | Index of the string containing the module. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | ModIdx | Module Index |  | uint16 |  |  | R | M | Index of the module within the string. | Indices are one-based.
Fixed Block |  | 4 | 2 | 1 | NCell | Module Cell Count |  | uint16 |  |  | R | M | Count of all cells in the module.
Fixed Block |  | 5 | 3 | 1 | SoC | Module SoC |  | uint16 | % | SoC_SF | R | O | Module state of charge, expressed as a percentage.
Fixed Block |  | 6 | 4 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth ofdischarge for the module. | Measurement.
Fixed Block |  | 7 | 5 | 1 | SoH | Module SoH |  | uint16 | % | SoH_SF | R | O | Module state of health, expressed as a percentage.
Fixed Block |  | 8 | 6 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Count of cycles executed.
Fixed Block |  | 10 | 8 | 1 | V | Module Voltage |  | uint16 | V | V_SF | R | M | Voltage of the module. | Measurement.
Fixed Block |  | 11 | 9 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the module. | Measurement.
Fixed Block |  | 12 | 10 | 1 | CellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the maximum voltage.
Fixed Block |  | 13 | 11 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the module. | Measurement.
Fixed Block |  | 14 | 12 | 1 | CellVMinCell | Min Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the minimum voltage.
Fixed Block |  | 15 | 13 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the module. | Calculation based on measurements.
Fixed Block |  | 16 | 14 | 1 | CellTmpMax | Max Cell Temperature |  | int16 | C | Tmp_SF | R | M | Maximum temperature for all cells in the module. | Measurement.
Fixed Block |  | 17 | 15 | 1 | CellTmpMaxCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with the maximum cell temperature.
Fixed Block |  | 18 | 16 | 1 | CellTmpMin | Min Cell Temperature |  | int16 | C | Tmp_SF | R | M | Minimum temperature for all cells in the module. | Measurement.
Fixed Block |  | 19 | 17 | 1 | CellTmpMinCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with the maximum cell temperature.
Fixed Block |  | 20 | 18 | 1 | CellTmpAvg | Average Cell Temperature |  | int16 | C | Tmp_SF | R | M | Average temperature for all cells in the module. | Calculation based on measurements.
Fixed Block |  | 21 | 19 | 1 | NCellBal | Balanced Cell Count |  | uint16 |  |  | R | O | Number of cells currently being balanced in the module.
Fixed Block |  | 22 | 20 | 16 | SN | Serial Number |  | string |  |  | R | O | Serial number for the module.
Fixed Block |  | 38 | 36 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | O | Scale factor for module state of charge.
Fixed Block |  | 39 | 37 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for module state of health.
Fixed Block |  | 40 | 38 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for module depth of discharge.
Fixed Block |  | 41 | 39 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for module voltage.
Fixed Block |  | 42 | 40 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 43 | 41 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperature.
Repeating Block |  | 44 | 0 | 1 | CellV | Cell Voltage |  | uint16 | V | CellV_SF | R | M | Cell terminal voltage. | Measurement.
Repeating Block |  | 45 | 1 | 1 | CellTmp | Cell Temperature |  | int16 | C | Tmp_SF | R | M | Cell temperature. | Measurement.
Repeating Block |  | 46 | 2 | 2 | CellSt | Cell Status |  | bitfield32 |  |  | R | O | Status of the cell.
bitfield32 | CellSt |  |  | Name: CELL_IS_BALANCING; Label: Cell Is Balancing; Value: 0 |  | Cell is currently being balanced.

## 806
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Model | 806 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BatTBD | Battery Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | BatStTBD | Battery String Points To Be Determined |  | uint16 |  |  | R | M

## 807
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery String Model | 807 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 34 + (RB Count * 24) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Idx | String Index |  | uint16 |  |  | R | M | Index of the string within the bank. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Number of modules in this string.
Fixed Block |  | 4 | 2 | 1 | NModCon | Connected Module Count |  | uint16 |  |  | R | M | Number of electrically connected modules in this string.
Fixed Block |  | 5 | 3 | 1 | ModVMax | Max Module Voltage |  | uint16 | V | ModV_SF | R | M | Maximum voltage for all modules in the string. | Measurement.
Fixed Block |  | 6 | 4 | 1 | ModVMaxMod | Max Module Voltage Module |  | uint16 |  |  | R | O | Module with the maximum voltage.
Fixed Block |  | 7 | 5 | 1 | ModVMin | Min Module Voltage |  | uint16 | V | ModV_SF | R | M | Minimum voltage for all modules in the string. | Measurement.
Fixed Block |  | 8 | 6 | 1 | ModVMinMod | Min Module Voltage Module |  | uint16 |  |  | R | O | Module with the minimum voltage.
Fixed Block |  | 9 | 7 | 1 | ModVAvg | Average Module Voltage |  | uint16 | V | ModV_SF | R | M | Average voltage for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 10 | 8 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the string. | Measurement.
Fixed Block |  | 11 | 9 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with the maximum voltage.
Fixed Block |  | 12 | 10 | 1 | CellVMaxStk | Max Cell Voltage Stack |  | uint16 |  |  | R | O | Stack containing the cell with the maximum voltage.
Fixed Block |  | 13 | 11 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the string. | Measurement.
Fixed Block |  | 14 | 12 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with the minimum voltage.
Fixed Block |  | 15 | 13 | 1 | CellVMinStk | Min Cell Voltage Stack |  | uint16 |  |  | R | O | Stack containing the cell with the minimum voltage.
Fixed Block |  | 16 | 14 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average voltage for all cells in the string. | Calculation based on measurements.
Fixed Block |  | 17 | 15 | 1 | TmpMax | Max Temperature |  | int16 | C | Tmp_SF | R | M | Maximum electrolyte temperature for all modules in the string. | Measurement.
Fixed Block |  | 18 | 16 | 1 | TmpMaxMod | Max Temperature Module |  | uint16 |  |  | R | O | Module with the maximum temperature.
Fixed Block |  | 19 | 17 | 1 | TmpMin | Min Temperature |  | int16 | C | Tmp_SF | R | M | Minimum electrolyte temperature for all modules in the string. | Measurement.
Fixed Block |  | 20 | 18 | 1 | TmpMinMod | Min Temperature Module |  | uint16 |  |  | R | O | Module with the minimum temperature.
Fixed Block |  | 21 | 19 | 1 | TmpAvg | Average Temperature |  | int16 | C | Tmp_SF | R | M | Average electrolyte temperature for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 22 | 20 | 2 | Evt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 24 | 22 | 2 | Evt2 | String Event 2 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 26 | 24 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 28 | 26 | 2 | EvtVnd2 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 30 | 28 | Size: 1; Name: ModV_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 31 | 29 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for voltage.
Fixed Block |  | 32 | 30 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M | Scale factor for temperature.
Fixed Block |  | 33 | 31 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge.
Fixed Block |  | 34 | 32 | Size: 1; Name: OCV_SF; Type: sunssf; R/W: R | M | Scale factor for open circuit voltage.
Fixed Block |  | 35 | 33 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 36 | 0 | 1 | ModIdx | Module Index |  | uint16 |  |  | R | M | Index of the module within the string. | Indices are one-based.
Repeating Block |  | 37 | 1 | 1 | ModNStk | Stack Count |  | uint16 |  |  | R | M | Number of stacks in this module.
Repeating Block |  | 38 | 2 | 2 | ModSt | Module Status |  | bitfield32 |  |  | R | M | Current status of the module.
Repeating Block |  | 40 | 4 | 1 | ModSoC | Module State of Charge |  | uint16 | % | SoC_SF | R | M | State of charge for this module.
Repeating Block |  | 41 | 5 | 1 | ModOCV | Open Circuit Voltage |  | uint16 | V | OCV_SF | R | M | Open circuit voltage for this module.
Repeating Block |  | 42 | 6 | 1 | ModV | External Voltage |  | uint16 | V | ModV_SF | R | M | External voltage fo this module.
Repeating Block |  | 43 | 7 | 1 | ModCellVMax | Maximum Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in this module. | Measurement.
Repeating Block |  | 44 | 8 | 1 | ModCellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the maximum cell voltage.
Repeating Block |  | 45 | 9 | 1 | ModCellVMin | Minimum Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in this module. | Measurement.
Repeating Block |  | 46 | 10 | 1 | ModCellVMinCell | Min Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the minimum cell voltage.
Repeating Block |  | 47 | 11 | 1 | ModCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average voltage for all cells in this module. | Calculation based on measurements.
Repeating Block |  | 48 | 12 | 1 | ModAnoTmp | Anolyte Temperature |  | uint16 | C | Tmp_SF | R | O
Repeating Block |  | 49 | 13 | 1 | ModCatTmp | Catholyte Temperature |  | uint16 | C | Tmp_SF | R | O
Repeating Block |  | 50 | 14 | 2 | ModConSt | Contactor Status |  | bitfield32 |  |  | R | O
Repeating Block |  | 52 | 16 | 2 | ModEvt1 | Module Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 54 | 18 | 2 | ModEvt2 | Module Event 2 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 56 | 20 | 1 | ModConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 57 | 21 | 1 | ModSetEna | Enable/Disable Module |  | enum16 |  |  | RW | O | Enables and disables the module. | Should reset to 0 upon completion.
Repeating Block |  | 58 | 22 | 1 | ModSetCon | Connect/Disconnect Module |  | enum16 |  |  | RW | O | Connects and disconnects the module. | Should reset to 0 upon completion.
Repeating Block |  | 59 | 23 | 1 | ModDisRsn | Disabled Reason |  | enum16 |  |  | R | O | Reason why the module is currently disabled.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Module is unable to communicate with the BMS or other components.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Module has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Module is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Module has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Module is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Module maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching module maximum charge current. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Module maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching module maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Module voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Module voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Module voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Module voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 13 |  | Module state of charge has reached or exceeded SoCMin.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 14 |  | Module state of charge is approaching SoCMin.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Alarm; Value: 15 |  | Module state of charge has reached or exceeded SoCMax.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 16 |  | Module state of charge is approaching SoCMax.
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the stacks in the module.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 18 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 19 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more module fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: RESERVED_3; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: FIRE_ALARM; Label: Fire Alarm; Value: 27 |  | A fire has been detected.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
bitfield32 | Evt2 |  |  | Name: LEAK_ALARM; Label: Leak Alarm; Value: 0 |  | A leak has been detected.
bitfield32 | Evt2 |  |  | Name: PUMP_ALARM; Label: Pump Alarm; Value: 1 |  | A pump has experienced an alarm condition or some other error.
bitfield32 | Evt2 |  |  | Name: HIGH_PRESSURE_ALARM; Label: High Pressure Alarm; Value: 2 |  | Pressure exceeds maximum value.
bitfield32 | Evt2 |  |  | Name: HIGH_PRESSURE_WARNING; Label: High Pressure Warning; Value: 3 |  | Pressure approaching maximum value.
bitfield32 | Evt2 |  |  | Name: LOW_FLOW_ALARM; Label: Low Flow Alarm; Value: 4 |  | Flow exceeds minimum value.
bitfield32 | Evt2 |  |  | Name: LOW_FLOW_WARNING; Label: Low Flow Warning; Value: 5 |  | Flow approaching minimum value.
bitfield32 | ModSt |  |  | Name: MODULE_ENABLED; Label: Module Is Enabled; Value: 0 |  | Module is enabled and will connect next time battery is asked to connect.
bitfield32 | ModSt |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | Module contactor is closed. | If module has multiple contactors, indicates that all contactors are closed.
bitfield32 | ModConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | ModConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | ModConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | ModConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | ModConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | ModConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | ModConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | ModConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | ModConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | ModConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | ModConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | ModConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | ModConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | ModConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | ModConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | ModConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | ModConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | ModConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | ModConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | ModConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | ModConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | ModConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | ModConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | ModConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | ModConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | ModConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | ModConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | ModConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | ModConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | ModConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | ModConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | ModEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Module is unable to communicate with the BMS or other components.
bitfield32 | ModEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Module has exceeded maximum operating temperature
bitfield32 | ModEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Module is approaching maximum operating temperature.
bitfield32 | ModEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Module has exceeded minimum operating temperature
bitfield32 | ModEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Module is approaching minimum operating temperature.
bitfield32 | ModEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Module maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching module maximum charge current. | See AChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Module maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching module maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Module voltage has exceeded maximum limit.
bitfield32 | ModEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Module voltage is approaching maximum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Module voltage has exceeded minimum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Module voltage is approaching minimum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 13 |  | Module state of charge has reached or exceeded SoCMin.
bitfield32 | ModEvt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 14 |  | Module state of charge is approaching SoCMin.
bitfield32 | ModEvt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Alarm; Value: 15 |  | Module state of charge has reached or exceeded SoCMax.
bitfield32 | ModEvt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 16 |  | Module state of charge is approaching SoCMax.
bitfield32 | ModEvt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the stacks in the module.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 18 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 19 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | ModEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more module fans has failed.
bitfield32 | ModEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | ModEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_3; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_4; Label: Reserved; Value: 25 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_5; Label: Reserved; Value: 26 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: FIRE_ALARM; Label: Fire Alarm; Value: 27 |  | A fire has been detected.
bitfield32 | ModEvt1 |  |  | Name: MODULE_CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery module has been configured incorrectly and will not operate.
bitfield32 | ModEvt1 |  |  | Name: MODULE_CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery module has been configured incorrectly and may not operate as expected.
bitfield32 | ModEvt2 |  |  | Name: LEAK_ALARM; Label: Leak Alarm; Value: 0 |  | A leak has been detected.
bitfield32 | ModEvt2 |  |  | Name: PUMP_ALARM; Label: Pump Alarm; Value: 1 |  | A pump has experienced an alarm condition or some other error.
bitfield32 | ModEvt2 |  |  | Name: HIGH_PRESSURE_ALARM; Label: High Pressure Alarm; Value: 2 |  | Pressure exceeds maximum value.
bitfield32 | ModEvt2 |  |  | Name: HIGH_PRESSURE_WARNING; Label: High Pressure Warning; Value: 3 |  | Pressure approaching maximum value.
bitfield32 | ModEvt2 |  |  | Name: LOW_FLOW_ALARM; Label: Low Flow Alarm; Value: 4 |  | Flow exceeds minimum value.
bitfield32 | ModEvt2 |  |  | Name: LOW_FLOW_WARNING; Label: Low Flow Warning; Value: 5 |  | Flow approaching minimum value.
enum16 | ModConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | ModConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | ModConFail |  |  | Name: MODULE_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | ModConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | ModConFail |  |  | Name: MODULE_NOT_ENABLED; Label: Module Not Enabled; Value: 4 |  | The module is not enabled.
enum16 | ModConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | ModConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | ModConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A failure during precharge occurred.
enum16 | ModConFail |  |  | Name: MODULE_FAULT; Label: Module Fault; Value: 8 |  | A module fault has occurred. | See ModEvt1 and ModEvt2 for more information.
enum16 | ModSetEna |  |  | Name: ENABLE_MODULE; Label: Enable Module; Value: 1 |  | Enable the module.
enum16 | ModSetEna |  |  | Name: DISABLE_MODULE; Label: Disable Module; Value: 2 |  | Disable the module.
enum16 | ModSetCon |  |  | Name: CONNECT_MODULE; Label: Connect Module; Value: 1 |  | Connect the module.
enum16 | ModSetCon |  |  | Name: DISCONNECT_MODULE; Label: Disconnect Module; Value: 2 |  | Disconnect the module.
enum16 | ModDisRsn |  |  | Name: NONE; Label: No Reason; Value: 0 |  | No reason provided.
enum16 | ModDisRsn |  |  | Name: FAULT; Label: Fault; Value: 1 |  | A fault has occurred which caused the module to be disabled.
enum16 | ModDisRsn |  |  | Name: MAINTENANCE; Label: Maintenance; Value: 2 |  | The module has been disabled for maintenance reasons.
enum16 | ModDisRsn |  |  | Name: EXTERNAL; Label: External; Value: 3 |  | The module has been disabled by an external user or controller.
enum16 | ModDisRsn |  |  | Name: OTHER; Label: Other; Value: 4 |  | The module has been disabled for some other reason.

## 808
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Module Model | 808 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModuleTBD | Module Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | StackTBD | Stack Points To Be Determined |  | uint16 |  |  | R | M

## 809
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Stack Model | 809 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | StackTBD | Stack Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | CellTBD | Cell Points To Be Determined |  | uint16 |  |  | R | M

## 63001
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | SunSpec Test Model 1 | 63001 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 134 + (RB Count * 18) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: sunssf_1; Type: sunssf; R/W: R | O
Fixed Block |  | 3 | 1 | Size: 1; Name: sunssf_2; Type: sunssf; R/W: R | O
Fixed Block |  | 4 | 2 | Size: 1; Name: sunssf_3; Type: sunssf; R/W: R | O
Fixed Block |  | 5 | 3 | Size: 1; Name: sunssf_4; Type: sunssf; R/W: R | O
Fixed Block |  | 6 | 4 | 1 | int16_1 |  |  | int16 |  | sunssf_1 | R | O
Fixed Block |  | 7 | 5 | 1 | int16_2 |  |  | int16 |  | sunssf_2 | R | O
Fixed Block |  | 8 | 6 | 1 | int16_3 |  |  | int16 |  | sunssf_3 | R | O
Fixed Block |  | 9 | 7 | 1 | int16_4 |  |  | int16 |  | sunssf_4 | RW | O
Fixed Block |  | 10 | 8 | Size: 1; Name: int16_5; Type: int16; R/W: R | O
Fixed Block |  | 11 | 9 | Size: 1; Name: int16_u; Type: int16; R/W: R | O
Fixed Block |  | 12 | 10 | 1 | uint16_1 |  |  | uint16 |  | sunssf_1 | R | O
Fixed Block |  | 13 | 11 | 1 | uint16_2 |  |  | uint16 |  | sunssf_2 | R | O
Fixed Block |  | 14 | 12 | 1 | uint16_3 |  |  | uint16 |  | sunssf_3 | R | O
Fixed Block |  | 15 | 13 | 1 | uint16_4 |  |  | uint16 |  | sunssf_4 | RW | O
Fixed Block |  | 16 | 14 | Size: 1; Name: uint16_5; Type: uint16; R/W: R | O
Fixed Block |  | 17 | 15 | Size: 1; Name: uint16_u; Type: uint16; R/W: R | O
Fixed Block |  | 18 | 16 | Size: 1; Name: acc16; Type: acc16; R/W: R | O
Fixed Block |  | 19 | 17 | Size: 1; Name: acc16_u; Type: acc16; R/W: R | O
Fixed Block |  | 20 | 18 | Size: 1; Name: enum16; Type: enum16; R/W: R | O
Fixed Block |  | 21 | 19 | Size: 1; Name: enum16_u; Type: enum16; R/W: R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: bitfield16; Type: bitfield16; R/W: R | O
Fixed Block |  | 23 | 21 | Size: 1; Name: bitfield16_u; Type: bitfield16; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | int32_1 |  |  | int32 |  | sunssf_5 | R | O
Fixed Block |  | 26 | 24 | 2 | int32_2 |  |  | int32 |  | sunssf_6 | R | O
Fixed Block |  | 28 | 26 | 2 | int32_3 |  |  | int32 |  | sunssf_7 | RW | O
Fixed Block |  | 30 | 28 | Size: 2; Name: int32_4; Type: int32; R/W: R | O
Fixed Block |  | 32 | 30 | Size: 2; Name: int32_5; Type: int32; R/W: R | O
Fixed Block |  | 34 | 32 | Size: 2; Name: int32_u; Type: int32; R/W: R | O
Fixed Block |  | 36 | 34 | 2 | uint32_1 |  |  | uint32 |  | sunssf_5 | R | O
Fixed Block |  | 38 | 36 | 2 | uint32_2 |  |  | uint32 |  | sunssf_6 | R | O
Fixed Block |  | 40 | 38 | 2 | uint32_3 |  |  | uint32 |  | sunssf_7 | RW | O
Fixed Block |  | 42 | 40 | 2 | uint32_4 |  |  | uint32 |  | 1 | R | O
Fixed Block |  | 44 | 42 | Size: 2; Name: uint32_5; Type: uint32; R/W: R | O
Fixed Block |  | 46 | 44 | Size: 2; Name: uint32_u; Type: uint32; R/W: R | O
Fixed Block |  | 48 | 46 | Size: 2; Name: acc32; Type: acc32; R/W: R | O
Fixed Block |  | 50 | 48 | Size: 2; Name: acc32_u; Type: acc32; R/W: R | O
Fixed Block |  | 52 | 50 | Size: 2; Name: enum32; Type: enum32; R/W: R | O
Fixed Block |  | 54 | 52 | Size: 2; Name: enum32_u; Type: enum32; R/W: R | O
Fixed Block |  | 56 | 54 | Size: 2; Name: bitfield32; Type: bitfield32; R/W: R | O
Fixed Block |  | 58 | 56 | Size: 2; Name: bitfield32_u; Type: bitfield32; R/W: R | O
Fixed Block |  | 60 | 58 | Size: 2; Name: ipaddr; Type: ipaddr; R/W: RW | O
Fixed Block |  | 62 | 60 | Size: 2; Name: ipaddr_u; Type: ipaddr; R/W: R | O
Fixed Block |  | 64 | 62 | Size: 4; Name: int64; Type: int64; R/W: RW | O
Fixed Block |  | 68 | 66 | Size: 4; Name: int64_u; Type: int64; R/W: R | O
Fixed Block |  | 72 | 70 | Size: 4; Name: acc64; Type: acc64; R/W: R | O
Fixed Block |  | 76 | 74 | Size: 4; Name: acc64_u; Type: acc64; R/W: R | O
Fixed Block |  | 80 | 78 | Size: 8; Name: ipv6addr; Type: ipv6addr; R/W: R | O
Fixed Block |  | 88 | 86 | Size: 8; Name: ipv6addr_u; Type: ipv6addr; R/W: R | O
Fixed Block |  | 96 | 94 | Size: 2; Name: float32; Type: float32; R/W: RW | O
Fixed Block |  | 98 | 96 | Size: 2; Name: float32_u; Type: float32; R/W: R | O
Fixed Block |  | 100 | 98 | Size: 16; Name: string; Type: string; R/W: RW | O
Fixed Block |  | 116 | 114 | Size: 16; Name: string_u; Type: string; R/W: R | O
Fixed Block |  | 132 | 130 | Size: 1; Name: sunssf_5; Type: sunssf; R/W: R | O
Fixed Block |  | 133 | 131 | Size: 1; Name: sunssf_6; Type: sunssf; R/W: R | O
Fixed Block |  | 134 | 132 | Size: 1; Name: sunssf_7; Type: sunssf; R/W: R | O
Fixed Block |  | 135 | 133 | Size: 1; Name: pad_1; Type: pad; R/W: R | O
Repeating Block |  | 136 | 0 | Size: 1; Name: sunssf_8; Type: sunssf; R/W: R | O
Repeating Block |  | 137 | 1 | 1 | int16_11 |  |  | int16 |  | sunssf_8 | RW | O
Repeating Block |  | 138 | 2 | 1 | int16_12 |  |  | int16 |  | sunssf_9 | R | O
Repeating Block |  | 139 | 3 | Size: 1; Name: int16_u; Type: int16; R/W: R | O
Repeating Block |  | 140 | 4 | 1 | uint16_11 |  |  | uint16 |  | sunssf_8 | RW | O
Repeating Block |  | 141 | 5 | 1 | uint16_12 |  |  | uint16 |  | sunssf_9 | R | O
Repeating Block |  | 142 | 6 | Size: 1; Name: uint16_13; Type: uint16; R/W: R | O
Repeating Block |  | 143 | 7 | Size: 1; Name: uint16_u; Type: uint16; R/W: R | O
Repeating Block |  | 144 | 8 | 2 | int32 |  |  | int32 |  | sunssf_1 | RW | O
Repeating Block |  | 146 | 10 | Size: 2; Name: int32_u; Type: int32; R/W: R | O
Repeating Block |  | 148 | 12 | 2 | uint32 |  |  | uint32 |  | sunssf_9 | RW | O
Repeating Block |  | 150 | 14 | Size: 2; Name: uint32_u; Type: uint32; R/W: R | O
Repeating Block |  | 152 | 16 | Size: 1; Name: sunssf_9; Type: sunssf; R/W: R | O
Repeating Block |  | 153 | 17 | Size: 1; Name: pad_2; Type: pad; R/W: R | O

## 63002
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | SunSpec Test Model 2 | 63002 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | (RB Count * 4) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | Size: 1; Name: sunssf_1; Type: sunssf; R/W: R | O
Repeating Block |  | 3 | 1 | 1 | int16_1 |  |  | int16 |  | sunssf_1 | RW | O
Repeating Block |  | 4 | 2 | 1 | int16_2 |  |  | int16 |  | sunssf_2 | R | O
Repeating Block |  | 5 | 3 | Size: 1; Name: sunssf_2; Type: sunssf; R/W: R | O

## 64001
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Veris Status and Configuration | 64001 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 71 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Cmd | Command Code |  | enum16 |  |  | RW | O
Fixed Block |  | 3 | 1 | 1 | HWRev | Hardware Revision |  | uint16 |  |  | R | O
Fixed Block |  | 4 | 2 | 1 | RSFWRev | RS FW Revision |  | uint16 |  |  | R | O
Fixed Block |  | 5 | 3 | 1 | OSFWRev | OS FW Revision |  | uint16 |  |  | R | O
Fixed Block |  | 6 | 4 | 2 | ProdRev | Product Revision |  | string |  |  | R | O
Fixed Block |  | 8 | 6 | 1 | Boots | Boot Count |  | uint16 |  |  | R | O
Fixed Block |  | 9 | 7 | 1 | Switch | DIP Switches |  | bitfield16 |  |  | R | O
Fixed Block |  | 10 | 8 | 1 | Sensors | Num Detected Sensors |  | uint16 |  |  | R | O
Fixed Block |  | 11 | 9 | 1 | Talking | Num Communicating Sensors |  | uint16 |  |  | R | O
Fixed Block |  | 12 | 10 | 1 | Status | System Status |  | bitfield16 |  |  | R | O
Fixed Block |  | 13 | 11 | 1 | Config | System Configuration |  | bitfield16 |  |  | R | O
Fixed Block |  | 14 | 12 | 1 | LEDblink | LED Blink Threshold |  | uint16 | Pct |  | R | O
Fixed Block |  | 15 | 13 | 1 | LEDon | LED On Threshold |  | uint16 | Pct |  | R | O
Fixed Block |  | 16 | 14 | Size: 1; Name: Reserved; Type: uint16; R/W: R | O
Fixed Block |  | 17 | 15 | 16 | Loc | Location String |  | string |  |  | R | O
Fixed Block |  | 33 | 31 | 1 | S1ID | Sensor 1 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 34 | 32 | 1 | S1Addr | Sensor 1 Address |  | uint16 |  |  | R | O
Fixed Block |  | 35 | 33 | 1 | S1OSVer | Sensor 1 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 36 | 34 | 2 | S1Ver | Sensor 1 Product Version |  | string |  |  | R | O
Fixed Block |  | 38 | 36 | 5 | S1Serial | Sensor 1 Serial Num |  | string |  |  | R | O
Fixed Block |  | 43 | 41 | 1 | S2ID | Sensor 2 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 44 | 42 | 1 | S2Addr | Sensor 2 Address |  | uint16 |  |  | R | O
Fixed Block |  | 45 | 43 | 1 | S2OSVer | Sensor 2 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 46 | 44 | 2 | S2Ver | Sensor 2 Product Version |  | string |  |  | R | O
Fixed Block |  | 48 | 46 | 5 | S2Serial | Sensor 2 Serial Num |  | string |  |  | R | O
Fixed Block |  | 53 | 51 | 1 | S3ID | Sensor 3 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 54 | 52 | 1 | S3Addr | Sensor 3 Address |  | uint16 |  |  | R | O
Fixed Block |  | 55 | 53 | 1 | S3OSVer | Sensor 3 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 56 | 54 | 2 | S3Ver | Sensor 3 Product Version |  | string |  |  | R | O
Fixed Block |  | 58 | 56 | 5 | S3Serial | Sensor 3 Serial Num |  | string |  |  | R | O
Fixed Block |  | 63 | 61 | 1 | S4ID | Sensor 4 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 64 | 62 | 1 | S4Addr | Sensor 4 Address |  | uint16 |  |  | R | O
Fixed Block |  | 65 | 63 | 1 | S4OSVer | Sensor 4 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 66 | 64 | 2 | S4Ver | Sensor 4 Product Version |  | string |  |  | R | O
Fixed Block |  | 68 | 66 | 5 | S4Serial | Sensor 4 Serial Num |  | string |  |  | R | O

## 64020
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Mersen GreenString | 64020 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 30 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Aux0Tmp | Aux 0 temperature |  | int16 | C |  | R | O
Fixed Block |  | 3 | 1 | 1 | Aux1Tmp | Aux 1 temperature |  | int16 | C |  | R | O
Fixed Block |  | 4 | 2 | 1 | Aux2Tmp | Aux 2 temperature |  | int16 | C |  | R | O
Fixed Block |  | 5 | 3 | 1 | Aux3Tmp | Aux 3 temperature |  | int16 | C |  | R | O
Fixed Block |  | 6 | 4 | 1 | Aux4Tmp | Aux 4 temperature |  | int16 | C |  | R | O
Fixed Block |  | 8 | 6 | 1 | ProbeTmp | Probe Temperature |  | int16 | C |  | R | M
Fixed Block |  | 7 | 5 | 1 | MainTmp | Main Temperature |  | int16 | C |  | R | M
Fixed Block |  | 9 | 7 | 1 | SensorV_SF | Voltage scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 10 | 8 | 1 | SensorA_SF | Current scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 11 | 9 | 1 | SensorHz_SF | Frequency scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 12 | 10 | 1 | Sensor1Voltage | Sensor1 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 13 | 11 | 1 | Sensor2Voltage | Sensor2 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 14 | 12 | 1 | Sensor3Voltage | Sensor3 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 15 | 13 | 1 | Sensor4Voltage | Sensor4 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 16 | 14 | 1 | Sensor5Voltage | Sensor5 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 17 | 15 | 1 | Sensor6Voltage | Sensor6 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 18 | 16 | 1 | Sensor7Voltage | Sensor7 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 19 | 17 | 1 | Sensor1Current | Sensor1 Current |  | int16 | A | SensorA_SF | R | O | scale of 4-20mA
Fixed Block |  | 20 | 18 | 1 | Sensor2Current | Sensor2 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 21 | 19 | 1 | Sensor3Current | Sensor3 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 22 | 20 | 1 | Sensor4Current | Sensor4 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 23 | 21 | 1 | Sensor5Current | Sensor5 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 24 | 22 | 1 | Sensor6Current | Sensor6 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 25 | 23 | 1 | Sensor7Current | Sensor7 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 26 | 24 | 1 | Sensor8 | Sensor8 frequency |  | uint16 | Hz | SensorHz_SF | R | O | frequency in Hz
Fixed Block |  | 27 | 25 | 1 | Relay1 | Relay 1 state |  | uint16 |  |  | R | O
Fixed Block |  | 28 | 26 | 1 | Relay2 | Relay 2 state |  | uint16 |  |  | R | O
Fixed Block |  | 29 | 27 | 1 | Relay3 | Relay 3 state |  | uint16 |  |  | R | O
Fixed Block |  | 30 | 28 | 1 | ResetAccumulators | Reset the accumulators |  | uint16 |  |  | R | O | always 0 in reading, used the code 0xC0DA during the writting for resetting them
Fixed Block |  | 31 | 29 | 1 | Reset | Reset the system |  | uint16 |  |  | R | O | always 0 in reading, used the code 0xC0DA during the writting for resetting the system
Repeating Block |  | 32 | 0 | 9 | SerialNumber | Serial number |  | string |  |  | R | M | strings of 16 caracters
Repeating Block |  | 41 | 9 | 6 | Firmware | Firmware version |  | string |  |  | R | M | string of 11 caracters
Repeating Block |  | 47 | 15 | 1 | Hardware | Hardware version |  | uint16 |  |  | R | M

## 64101
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Eltek Inverter Extension | 64101 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 7 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: Eltek_Country_Code; Type: uint16; R/W: R | O
Fixed Block |  | 3 | 1 | Size: 1; Name: Eltek_Feeding_Phase; Type: uint16; R/W: R | O
Fixed Block |  | 4 | 2 | Size: 1; Name: Eltek_APD_Method; Type: uint16; R/W: R | O
Fixed Block |  | 5 | 3 | Size: 1; Name: Eltek_APD_Power_Ref; Type: uint16; R/W: R | O
Fixed Block |  | 6 | 4 | Size: 1; Name: Eltek_RPS_Method; Type: uint16; R/W: R | O
Fixed Block |  | 7 | 5 | Size: 1; Name: Eltek_RPS_Q_Ref; Type: uint16; R/W: R | O
Fixed Block |  | 8 | 6 | Size: 1; Name: Eltek_RPS_CosPhi_Ref; Type: int16; R/W: R | O

## 64110
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | OutBack AXS device | 64110 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 282 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | MajorFWRev | AXS Major Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | 1 | MidFWRev | AXS Mid Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 4 | 2 | 1 | MinorFWRev | AXS Minor Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 5 | 3 | 1 | EncrypKey | Encryption Key |  | uint16 |  |  | R | M
Fixed Block |  | 6 | 4 | 7 | MAC_Address | MAC Address |  | string |  |  | R | M
Fixed Block |  | 13 | 11 | 8 | WritePassword | Write Password |  | string |  |  | R | M
Fixed Block |  | 21 | 19 | 1 | EnableDHCP | Enable DHCP |  | enum16 |  |  | R | M
Fixed Block |  | 22 | 20 | 2 | TCPIP_address | TCPIP Address |  | ipaddr |  |  | R | M
Fixed Block |  | 24 | 22 | 2 | Gateway_address | TCPIP Gateway |  | ipaddr |  |  | R | M
Fixed Block |  | 26 | 24 | 2 | TCPIP_Netmask | TCPIP Netmask |  | ipaddr |  |  | R | M
Fixed Block |  | 28 | 26 | 2 | DNS1_address | TCPIP DNS1 |  | ipaddr |  |  | R | M
Fixed Block |  | 30 | 28 | 2 | DNS2_address | TCPIP DNS2 |  | ipaddr |  |  | R | M
Fixed Block |  | 32 | 30 | 1 | Modbus_port | ModBus Port |  | uint16 |  |  | R | M
Fixed Block |  | 33 | 31 | 20 | SMTP_server_nm | SMTP Server Name |  | string |  |  | R | M
Fixed Block |  | 53 | 51 | 16 | SMTP_account_nm | SMTP Account Name |  | string |  |  | R | M
Fixed Block |  | 69 | 67 | 1 | SMTP_enable_SSL | Enable SMTP SSL |  | enum16 |  |  | R | M
Fixed Block |  | 70 | 68 | 8 | SMTP_password | SMTP Password |  | string |  |  | R | M
Fixed Block |  | 78 | 76 | 20 | SMTP_user_nm | SMTP User Name |  | string |  |  | R | M
Fixed Block |  | 98 | 96 | 1 | Stat_email_int | Status Email Interval |  | uint16 |  |  | R | M
Fixed Block |  | 99 | 97 | 1 | Stat_start_HR | Status Email Start Hour |  | uint16 |  |  | R | M
Fixed Block |  | 100 | 98 | 25 | Stat_email_sub | Status Email Subject |  | string |  |  | R | M
Fixed Block |  | 125 | 123 | 20 | Stat_email_addr1 | Status Email to Address 1 |  | string |  |  | R | M
Fixed Block |  | 145 | 143 | 20 | Stat_email_addr2 | Status Email to Address 2 |  | string |  |  | R | M
Fixed Block |  | 165 | 163 | 1 | Alarm_email_en | Enable Alarm Email |  | enum16 |  |  | R | M
Fixed Block |  | 166 | 164 | 25 | Alarm_email_sub | Alarm Email Subject |  | string |  |  | R | M
Fixed Block |  | 191 | 189 | 20 | Alarm_email_addr1 | Alarm Email to Address 1 |  | string |  |  | R | M
Fixed Block |  | 211 | 209 | 20 | Alarm_email_addr2 | Alarm Email to Address 2 |  | string |  |  | R | M
Fixed Block |  | 231 | 229 | 8 | FTP_password | FTP Password |  | string |  |  | R | M
Fixed Block |  | 239 | 237 | 8 | TELNET_password | Telnet Password |  | string |  |  | R | M
Fixed Block |  | 247 | 245 | 1 | Log_write_int | SD-Card Datalog Write Interval |  | uint16 | Tms |  | R | M
Fixed Block |  | 248 | 246 | 1 | Log_retain | SD-Card Datalog Retain |  | uint16 | Tmd |  | R | M
Fixed Block |  | 249 | 247 | 1 | Log_mode | SD-Card Datalog Mode |  | enum16 |  |  | R | M
Fixed Block |  | 250 | 248 | 20 | NTP_server_nm | NTP Timer Server Name |  | string |  |  | R | M
Fixed Block |  | 270 | 268 | 1 | NTP_enable | Enable Network Time |  | enum16 |  |  | R | M
Fixed Block |  | 271 | 269 | 1 | TimeZone | Time Zone |  | int16 | Tmh |  | R | M
Fixed Block |  | 272 | 270 | 1 | Date_year | Year |  | uint16 |  |  | R | M
Fixed Block |  | 273 | 271 | 1 | Date_month | Month |  | uint16 |  |  | R | M
Fixed Block |  | 274 | 272 | 1 | Date_Day | Day |  | uint16 |  |  | R | M
Fixed Block |  | 275 | 273 | 1 | Time_hour | Hour |  | uint16 |  |  | R | M
Fixed Block |  | 276 | 274 | 1 | Time_minute | Minute |  | uint16 |  |  | R | M
Fixed Block |  | 277 | 275 | 1 | Time_second | Second |  | uint16 |  |  | R | M
Fixed Block |  | 278 | 276 | 1 | Battery_temp | Battery Temperature |  | int16 | C | Temp_SF | R | M
Fixed Block |  | 279 | 277 | 1 | Ambient_temp | Ambient Temperature |  | int16 | C | Temp_SF | R | M
Fixed Block |  | 280 | 278 | Size: 1; Name: Temp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 281 | 279 | 1 | AXS_Error | AXS Error |  | bitfield16 |  |  | R | M
Fixed Block |  | 282 | 280 | 1 | AXS_Status | AXS Status |  | bitfield16 |  |  | R | M
Fixed Block |  | 283 | 281 | 1 | AXS_Spare | Spare |  | uint16 |  |  | R | M
enum16 | SMTP_enable_SSL |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | SMTP_enable_SSL |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1
enum16 | Alarm_email_en |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | Alarm_email_en |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1
enum16 | Log_mode |  |  | Name: LOG_DISABLED; Label: Disabled; Value: 0
enum16 | Log_mode |  |  | Name: LOG_EXCEL; Label: Excel; Value: 1
enum16 | Log_mode |  |  | Name: LOG_COMPACT; Label: Compact; Value: 2
enum16 | NTP_enable |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | NTP_enable |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1

## 64111
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Charge Controller | 64111 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 23 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Port | Port Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 4 | 2 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 5 | 3 | Size: 1; Name: P_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 6 | 4 | Size: 1; Name: AH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: KWH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 8 | 6 | 1 | BattV | Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 9 | 7 | 1 | ArrayV | Array Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 10 | 8 | 1 | OutputA | Output Current |  | uint16 | A | A_SF | R | M
Fixed Block |  | 11 | 9 | 1 | InputA | Array Current |  | uint16 | A | P_SF | R | M
Fixed Block |  | 12 | 10 | 1 | ChargerSt | Operating State |  | enum16 |  |  | R | M
Fixed Block |  | 13 | 11 | 1 | OutputW | Output Wattage |  | uint16 | W | P_SF | R | M
Fixed Block |  | 14 | 12 | 1 | TodayMinBatV | Todays Minimum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | 1 | TodayMaxBatV | Todays Maximum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 16 | 14 | 1 | VOCV | VOC |  | uint16 | V | V_SF | R | M
Fixed Block |  | 17 | 15 | 1 | TodayMaxVOC | Todays Maximum VOC |  | uint16 | V | V_SF | R | M
Fixed Block |  | 18 | 16 | 1 | TodaykWhOutput | Todays kWh |  | uint16 | kWh | KWH_SF | R | M
Fixed Block |  | 19 | 17 | 1 | TodayAHOutput | Todays AH |  | uint16 | AH | AH_SF | R | M
Fixed Block |  | 20 | 18 | 1 | LifeTimeKWHOut | Lifetime kWh |  | uint16 | kWh | P_SF | R | M
Fixed Block |  | 21 | 19 | 1 | LifeTimeAHOut | Lifetime kAH |  | uint16 | kAH | KWH_SF | R | M
Fixed Block |  | 22 | 20 | 1 | LifeTimeMaxOut | Lifetime Maximum Output Wattage |  | uint16 | W | P_SF | R | M
Fixed Block |  | 23 | 21 | 1 | LifeTimeMaxBatt | Lifetime Maximum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 24 | 22 | 1 | LifeTimeMaxVOC | Lifetime Maximum VOC Voltage |  | uint16 | V | V_SF | R | M
enum16 | ChargerSt |  |  | Name: Off; Label: Off; Value: 0
enum16 | ChargerSt |  |  | Name: Float; Label: Float Charging; Value: 1
enum16 | ChargerSt |  |  | Name: Bulk; Label: Bulk Charging; Value: 2
enum16 | ChargerSt |  |  | Name: Absorb; Label: Absorb Charging; Value: 3
enum16 | ChargerSt |  |  | Name: EQ; Label: Equilize Charging; Value: 4

## 64112
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | OutBack FM Charge Controller | 64112 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 64 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Port | Port Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 4 | 2 | Size: 1; Name: C_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 5 | 3 | Size: 1; Name: H_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 6 | 4 | Size: 1; Name: P_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: AH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 8 | 6 | Size: 1; Name: KWH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 9 | 7 | 1 | CC_Config_fault | Faults |  | bitfield16 |  |  | R | M
Fixed Block |  | 10 | 8 | 1 | CC_Config_absorb_V | Absorb |  | uint16 | V | V_SF | R | M
Fixed Block |  | 11 | 9 | 1 | CC_Config_absorb_Hr | Absorb Time |  | uint16 | Tmh | H_SF | R | M
Fixed Block |  | 12 | 10 | 1 | CC_Config_absorb_End_A | Absorb End |  | uint16 | A | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | CC_Config_rebulk_V | Rebulk |  | uint16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | CC_Config_float_V | Float |  | uint16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | 1 | CC_Config_max_Chg_A | Maximum Charge |  | uint16 | A | V_SF | R | M
Fixed Block |  | 16 | 14 | 1 | CC_Config_equalize_V | Equalize |  | uint16 | V | V_SF | R | M
Fixed Block |  | 17 | 15 | 1 | CC_Config_equalize_Hr | Equalize Time |  | uint16 | Tmh |  | R | M
Fixed Block |  | 18 | 16 | 1 | CC_Config_auto_equalize | Auto Equalize Interval |  | uint16 | Tmd |  | R | M
Fixed Block |  | 19 | 17 | 1 | CC_Config_MPPT_mode | MPPT mode |  | enum16 |  |  | R | M
Fixed Block |  | 20 | 18 | 1 | CC_Config_sweep_width | Sweep Width |  | enum16 |  |  | R | M
Fixed Block |  | 21 | 19 | 1 | CC_Config_sweep_max | Sweep Maximum |  | enum16 |  |  | R | M
Fixed Block |  | 22 | 20 | 1 | CC_Config_U_Pick_Duty_cyc | U-Pick PWM Duty Cycle |  | uint16 | Pct | V_SF | R | M
Fixed Block |  | 23 | 21 | 1 | CC_Config_grid_tie | Grid Tie Mode |  | enum16 |  |  | R | M
Fixed Block |  | 24 | 22 | 1 | CC_Config_temp_comp | Temp Comp Mode |  | enum16 |  |  | R | M
Fixed Block |  | 25 | 23 | 1 | CC_Config_temp_comp_llimt | Temp Comp Lower Limit |  | uint16 | V | V_SF | R | M
Fixed Block |  | 26 | 24 | 1 | CC_Config_temp_comp_hlimt | Temp Comp Upper Limit |  | uint16 | V | V_SF | R | M
Fixed Block |  | 27 | 25 | 1 | CC_Config_auto_restart | Auto Restart Mode |  | enum16 |  |  | R | M
Fixed Block |  | 28 | 26 | 1 | CC_Config_wakeup_VOC | Wakeup VOC Change |  | uint16 | V | V_SF | R | M
Fixed Block |  | 29 | 27 | 1 | CC_Config_snooze_mode_A | Snooze Mode |  | uint16 | A | V_SF | R | M
Fixed Block |  | 30 | 28 | 1 | CC_Config_wakeup_interval | Wakeup Interval |  | uint16 | Tms |  | R | M
Fixed Block |  | 31 | 29 | 1 | CC_Config_AUX_mode | AUX Output Mode |  | enum16 |  |  | R | M
Fixed Block |  | 32 | 30 | 1 | CC_Config_AUX_control | AUX Output Control |  | enum16 |  |  | R | M
Fixed Block |  | 33 | 31 | 1 | CC_Config_AUX_state | AUX Output State |  | enum16 |  |  | R | M
Fixed Block |  | 34 | 32 | 1 | CC_Config_AUX_polarity | AUX Output Polarity |  | enum16 |  |  | R | M
Fixed Block |  | 35 | 33 | 1 | CC_Config_AUX_L_Batt_disc | AUX Low Battery Disconnect |  | uint16 | V | V_SF | R | M
Fixed Block |  | 36 | 34 | 1 | CC_Config_AUX_L_Batt_rcon | AUX Low Battery Reconnect |  | uint16 | V | V_SF | R | M
Fixed Block |  | 37 | 35 | 1 | CC_Config_AUX_L_Batt_dly | AUX Low Battery Disconnect Delay |  | uint16 | Tms |  | R | M
Fixed Block |  | 38 | 36 | 1 | CC_Config_AUX_Vent_fan_V | AUX Vent Fan |  | uint16 | V | V_SF | R | M
Fixed Block |  | 39 | 37 | 1 | CC_Config_AUX_PV_triggerV | AUX PV Trigger |  | uint16 | V | V_SF | R | M
Fixed Block |  | 40 | 38 | 1 | CC_Config_AUX_PV_trg_h_tm | AUX PV Trigger Hold Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 41 | 39 | 1 | CC_Config_AUX_Nlite_ThrsV | AUX Night Light Threshold |  | uint16 | V | V_SF | R | M
Fixed Block |  | 42 | 40 | 1 | CC_Config_AUX_Nlite_On_tm | AUX Night Light On Time |  | uint16 | Tmh | H_SF | R | M
Fixed Block |  | 43 | 41 | 1 | CC_Config_AUX_Nlite_On_hist | AUX Night Light On Hysterisis |  | uint16 | Tms |  | R | M
Fixed Block |  | 44 | 42 | 1 | CC_Config_AUX_Nlite_Off_hist | AUX Night Light Off Hysterisis |  | uint16 | Tms |  | R | M
Fixed Block |  | 45 | 43 | 1 | CC_Config_AUX_Error_batt_V | AUX Error Output Low Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 46 | 44 | 1 | CC_Config_AUX_Divert_h_time | AUX Divert Hold Time |  | uint16 | Tms | V_SF | R | M
Fixed Block |  | 47 | 45 | 1 | CC_Config_AUX_Divert_dly_time | AUX Divert Delay Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 48 | 46 | 1 | CC_Config_AUX_Divert_Rel_V | AUX Divert Relative |  | uint16 | V | V_SF | R | M
Fixed Block |  | 49 | 47 | 1 | CC_Config_AUX_Divert_Hyst_V | AUX Divert Hysterisis |  | uint16 | V | V_SF | R | M
Fixed Block |  | 50 | 48 | 1 | CC_Config_MajorFWRev | FM CC Major Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 51 | 49 | 1 | CC_Config_MidFWRev | FM CC Mid Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 52 | 50 | 1 | CC_Config_MinorFWRev | FM CC Minor Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 53 | 51 | 1 | CC_Config_DataLog_Day_offset | Set Data Log Day Offset |  | uint16 | Tmd |  | R | M
Fixed Block |  | 54 | 52 | 1 | CC_Config_DataLog_Cur_Day_off | Current Data Log Day Offset |  | uint16 | Tmd |  | R | M
Fixed Block |  | 55 | 53 | 1 | CC_Config_DataLog_Daily_AH | Data Log Daily |  | uint16 | Ah |  | R | M
Fixed Block |  | 56 | 54 | 1 | CC_Config_DataLog_Daily_KWH | Data Log Daily |  | uint16 | kWh | KWH_SF | R | M
Fixed Block |  | 57 | 55 | 1 | CC_Config_DataLog_Max_Out_A | Data Log Daily Maximum Output |  | uint16 | A | V_SF | R | M
Fixed Block |  | 58 | 56 | 1 | CC_Config_DataLog_Max_Out_W | Data Log Daily Maximum Output |  | uint16 | W | V_SF | R | M
Fixed Block |  | 59 | 57 | 1 | CC_Config_DataLog_Absorb_T | Data Log Daily Absorb Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 60 | 58 | 1 | CC_Config_DataLog_Float_T | Data Log Daily Float Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 61 | 59 | 1 | CC_Config_DataLog_Min_Batt_V | Data Log Daily Minimum Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 62 | 60 | 1 | CC_Config_DataLog_Max_Batt_V | Data Log Daily Maximum Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 63 | 61 | 1 | CC_Config_DataLog_Max_Input_V | Data Log Daily Maximum Input |  | uint16 | V | V_SF | R | M
Fixed Block |  | 64 | 62 | 1 | CC_Config_DataLog_Clear | Data Log Clear |  | uint16 |  |  | R | M
Fixed Block |  | 65 | 63 | 1 | CC_Config_DataLog_Clr_Comp | Data Log Clear Complement |  | uint16 |  |  | R | M
enum16 | CC_Config_MPPT_mode |  |  | Name: Auto; Label: Auto; Value: 1
enum16 | CC_Config_MPPT_mode |  |  | Name: U_Pick; Label: U-Pick; Value: 1
enum16 | CC_Config_MPPT_mode |  |  | Name: Wind; Label: Wind; Value: 2
enum16 | CC_Config_sweep_width |  |  | Name: Half; Label: Half; Value: 0
enum16 | CC_Config_sweep_width |  |  | Name: Full; Label: Full; Value: 1
enum16 | CC_Config_sweep_max |  |  | Name: Eighty_Percent; Label: 80 %; Value: 0
enum16 | CC_Config_sweep_max |  |  | Name: Eighty_Five_Percent; Label: 85 %; Value: 1
enum16 | CC_Config_sweep_max |  |  | Name: Ninty_Percent; Label: 90 %; Value: 2
enum16 | CC_Config_sweep_max |  |  | Name: Ninty_Nine_Percent; Label: 99 %; Value: 3
enum16 | CC_Config_grid_tie |  |  | Name: Disabled; Label: Disabled; Value: 0
enum16 | CC_Config_grid_tie |  |  | Name: Enabled; Label: Enabled; Value: 1
enum16 | CC_Config_temp_comp |  |  | Name: Wide; Label: Wide; Value: 0
enum16 | CC_Config_temp_comp |  |  | Name: Limited; Label: Limited; Value: 1
enum16 | CC_Config_auto_restart |  |  | Name: Off; Label: Off; Value: 0
enum16 | CC_Config_auto_restart |  |  | Name: Every_90_Minutes; Label: Every 90 Minutes; Value: 1
enum16 | CC_Config_auto_restart |  |  | Name: Every_90_Minutes_if_Absorb_or_Float; Label: Every 90 Minutes if Absorb or Float; Value: 2
enum16 | CC_Config_AUX_mode |  |  | Name: Float; Label: Float; Value: 0
enum16 | CC_Config_AUX_mode |  |  | Name: Diversion_Relay; Label: Diversion: Relay; Value: 1
enum16 | CC_Config_AUX_mode |  |  | Name: Diversion_Solid_St; Label: Diversion: Solid St; Value: 2
enum16 | CC_Config_AUX_mode |  |  | Name: Low_Batt_Disconnect; Label: Low Batt Disconnect; Value: 3
enum16 | CC_Config_AUX_mode |  |  | Name: Remote; Label: Remote; Value: 4
enum16 | CC_Config_AUX_mode |  |  | Name: Vent_Fan; Label: Vent Fan; Value: 5
enum16 | CC_Config_AUX_mode |  |  | Name: PV_Trigger; Label: PV Trigger; Value: 6
enum16 | CC_Config_AUX_mode |  |  | Name: Error_Output; Label: Alarm Output; Value: 7
enum16 | CC_Config_AUX_mode |  |  | Name: Night_Light; Label: Night Light; Value: 8
enum16 | CC_Config_AUX_control |  |  | Name: Off; Label: Off; Value: 0
enum16 | CC_Config_AUX_control |  |  | Name: Auto; Label: Auto; Value: 1
enum16 | CC_Config_AUX_control |  |  | Name: On; Label: On; Value: 2
enum16 | CC_Config_AUX_state |  |  | Name: Disabled; Label: Disabled; Value: 0
enum16 | CC_Config_AUX_state |  |  | Name: Enabled; Label: Enabled; Value: 1
enum16 | CC_Config_AUX_polarity |  |  | Name: Low; Label: Low; Value: 0
enum16 | CC_Config_AUX_polarity |  |  | Name: High; Label: High; Value: 1

## 64400
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Parameter Read / Write | 64400 | uint16 |  |  | R | M | Special Model to read and write Studer-Innotec device parameters
Header |  | 1 |  | 1 | L |  | 6 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ParNum | Parameter Number |  | uint16 |  |  | RW | M | Parameter number to be read or written (input)
Fixed Block |  | 3 | 1 | 1 | ParType | Parameter Type |  | enum16 |  |  | RW | M | Type of value, corresponding to the parameter (READ: output, WRITE: input) | This type is used for data transfer between Solar Monitor and Studer, see ParValue for its notes.
Fixed Block |  | 4 | 2 | 2 | ParValue | Parameter Value |  | float32 |  |  | RW | M | Read value (output) or value to be written (input) | This value is always in Float32 format.
Fixed Block |  | 6 | 4 | 1 | ParCmd | Parameter Command |  | bitfield16 |  |  | RW | M | Command to be issued (read or write command is set and then this field is polled until the bit gets cleared)
Fixed Block |  | 7 | 5 | 1 | ParCast | Parameter Cast |  | enum16 |  |  | RW | M | Cast determines phase, unicast or multicast
enum16 | ParType |  |  | Name: Integer; Label: Integer32; Value: 0 |  | 32 bit signed value, big endian | Studer INT32 type.
enum16 | ParType |  |  | Name: Enum; Label: Enum16; Value: 1 |  | 32 bit signed value, only 16 bits used | Studer SHORT_ENUM type.
enum16 | ParType |  |  | Name: Byte; Label: Integer8; Value: 2 |  | 32 bit signed value, only 8 bits used | Studer BOOL type.
enum16 | ParType |  |  | Name: Float; Label: Float32; Value: 3 |  | float in 32 bit IEEE 754 format, big endian | Studer FLOAT type.
bitfield16 | ParCmd |  |  | Name: READ; Label: Read Command; Value: 32 |  | Set this bit to initiate a read operation | Also the ParNum field must be written previously or concurrently. ParType and ParValue is an ouput from this command.
bitfield16 | ParCmd |  |  | Name: WRITE; Label: Write Command; Value: 16 |  | Set this bit to initiate a write operation | All 3 other fields ParNum, ParType and ParValue must be written previously or concurrently.
enum16 | ParCast |  |  | Name: MultiCast; Label: All phases multicast; Value: 0 |  | for all phases (multicast)
enum16 | ParCast |  |  | Name: Phase1; Label: Phase 1; Value: 1 |  | for phase 1 only
enum16 | ParCast |  |  | Name: Phase2; Label: Phase 2; Value: 2 |  | for phase 2 only
enum16 | ParCast |  |  | Name: Phase3; Label: Phase 3; Value: 3 |  | for phase 3 only
enum16 | ParCast |  |  | Name: UniCast; Label: All phases unicast; Value: 4 |  | for all phases (unicast) | cannot be used for system device

## 64401
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer System Model | 64401 | uint16 |  |  | R | M | Studer-Innotec System Model
Header |  | 1 |  | 1 | L |  | 64 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | sysBatteryVoltage | Battery Voltage |  | float32 |  |  | R | O | {7000};If no BSP(601) present, get from 100 {3000}, if not present get from 300 {11000}, in not present get from 700 {15000}
Fixed Block |  | 4 | 2 | 2 | sysBatteryTemp | Battery Temperature |  | float32 |  |  | R | O | {7029};If no BSP(601) present, get from 100 {3001}, if not present get from 300 {11005}, in not present get from 700 {15032}
Fixed Block |  | 6 | 4 | 2 | sysBatteryCurrent | Battery Current |  | float32 |  |  | R | O | {7001};If no BSP present, add all Ibatt of all XT, VT and VS
Fixed Block |  | 8 | 6 | 2 | sysStateOfCharge | State of Charge |  | float32 |  |  | R | O | {7032};ONLY if BSP present
Fixed Block |  | 10 | 8 | 2 | sysChargedToday | Charged Today |  | float32 |  |  | R | O | {7007};ONLY if BSP present
Fixed Block |  | 12 | 10 | 2 | sysDischargedToday | Discharged Today |  | float32 |  |  | R | O | {7008};ONLY if BSP present
Fixed Block |  | 14 | 12 | 2 | sysPVPower | PV Power |  | float32 |  |  | R | O | {11004}+ {15010};Add PV power of all VarioTracks + VarioStrings
Fixed Block |  | 16 | 14 | 2 | sysPVChargingCurrent | PV Charging Current |  | float32 |  |  | R | O | {11001}+ {15001};Add battery current of all VarioTracks + VarioStrings
Fixed Block |  | 18 | 16 | 2 | sysPVEnergyToday | PV Energy Today |  | float32 |  |  | R | O | {11007}+ {15017};Add all daily production of alll VT + VS

## 64402
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer System Phase Value Model | 64402 | uint16 |  |  | R | M | Studer-Innotec System Phase Value Model
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 33) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RB Count |  | 3 | uint16 |  |  | R | O | Number of Blocks (Phases)
Repeating Block |  | 3 | 0 | 1 | sysPhase | Phase | 0 | uint16 |  |  | R | O | Phase L1
Repeating Block |  | 4 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@191]
Repeating Block |  | 6 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@191]
Repeating Block |  | 8 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@191]
Repeating Block |  | 10 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@191]
Repeating Block |  | 12 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@191]
Repeating Block |  | 14 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@191]
Repeating Block |  | 16 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@191]
Repeating Block |  | 18 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@191]
Repeating Block |  | 20 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@191]
Repeating Block |  | 22 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@191]
Repeating Block |  | 24 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@191]
Repeating Block |  | 26 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@191]
Repeating Block |  | 28 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@191]
Repeating Block |  | 30 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@191]
Repeating Block |  | 32 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@191]
Repeating Block |  | 34 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@191]
Repeating Block |  | 36 | 0 | 1 | sysPhase | Phase | 1 | uint16 |  |  | R | O | Phase L2
Repeating Block |  | 37 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@192]
Repeating Block |  | 39 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@192]
Repeating Block |  | 41 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@192]
Repeating Block |  | 43 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@192]
Repeating Block |  | 45 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@192]
Repeating Block |  | 47 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@192]
Repeating Block |  | 49 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@192]
Repeating Block |  | 51 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@192]
Repeating Block |  | 53 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@192]
Repeating Block |  | 55 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@192]
Repeating Block |  | 57 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@192]
Repeating Block |  | 59 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@192]
Repeating Block |  | 61 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@192]
Repeating Block |  | 63 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@192]
Repeating Block |  | 65 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@192]
Repeating Block |  | 67 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@192]
Repeating Block |  | 69 | 0 | 1 | sysPhase | Phase | 2 | uint16 |  |  | R | O | Phase L3
Repeating Block |  | 70 | 1 | 2 | sysInVoltage | Input Voltage |  | float32 | V |  | R | O | 3113 [@193]
Repeating Block |  | 72 | 3 | 2 | sysInVoltageMin | Input Voltage Min |  | float32 | V |  | R | O | 3011 [@193]
Repeating Block |  | 74 | 5 | 2 | sysInVoltageMax | Input Voltage Max |  | float32 | V |  | R | O | 3012 [@193]
Repeating Block |  | 76 | 7 | 2 | sysInCurrent | Input Current |  | float32 | A |  | R | O | 3116 [@193]
Repeating Block |  | 78 | 9 | 2 | sysInCurrentMin | Input Current Min |  | float32 | A |  | R | O | 3114 [@193]
Repeating Block |  | 80 | 11 | 2 | sysInCurrentMax | Input Current Max |  | float32 | A |  | R | O | 3115 [@193]
Repeating Block |  | 82 | 13 | 2 | sysInFrequency | Input Frequency |  | float32 | Hz |  | R | O | 3122 [@193]
Repeating Block |  | 84 | 15 | 2 | sysInFrequencyMin | Input Frequency Min |  | float32 | Hz |  | R | O | 3120 [@193]
Repeating Block |  | 86 | 17 | 2 | sysInFrequencyMax | Input Frequency Max |  | float32 | Hz |  | R | O | 3121 [@193]
Repeating Block |  | 88 | 19 | 2 | sysInApparentPower | Input Power |  | float32 | kVA |  | R | O | 3013 [@193]
Repeating Block |  | 90 | 21 | 2 | sysInActivePower | Input Active Power |  | float32 | W |  | R | O | 3088 [@193]
Repeating Block |  | 92 | 23 | 2 | sysOutVoltage | Output Voltage |  | float32 | V |  | R | O | 3021 [@193]
Repeating Block |  | 94 | 25 | 2 | sysOutCurrent | Output Current |  | float32 | A |  | R | O | 3022 [@193]
Repeating Block |  | 96 | 27 | 2 | sysOutFrequency | Output Frequency |  | float32 | Hz |  | R | O | 3085 [@193]
Repeating Block |  | 98 | 29 | 2 | sysOutApparentPower | Output Power |  | float32 | kVA |  | R | O | 3023 [@193]
Repeating Block |  | 100 | 31 | 2 | sysOutActivePower | Output Active Power |  | float32 | W |  | R | O | 3087 [@193]

## 64403
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Event Model | 64403 | uint16 |  |  | R | M | Studer-Innotec Event Model
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 5) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RB Count |  | 10 | uint16 |  |  | R | O | Number of Blocks
Repeating Block |  | 3 | 1 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 5 | 3 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 7 | 5 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 8 | 6 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 10 | 8 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 12 | 10 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 13 | 11 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 15 | 13 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 17 | 15 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 18 | 16 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 20 | 18 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 22 | 20 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 23 | 21 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 25 | 23 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 27 | 25 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 28 | 26 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 30 | 28 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 32 | 30 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 33 | 31 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 35 | 33 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 37 | 35 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 38 | 36 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 40 | 38 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 42 | 40 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 43 | 41 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 45 | 43 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 47 | 45 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
Repeating Block |  | 48 | 46 | 2 | evtDevAddr | Device Address |  | uint32 |  |  | R | O | Source address of the most recent message – originating device address. | See the Xtender seriál protocol 3.5 Addressing the devices.
Repeating Block |  | 50 | 48 | 2 | evtTimeStamp | Timestamp |  | uint32 |  |  | R | O | The time at which the message occurred in seconds since January 1, 1970.
Repeating Block |  | 52 | 50 | 1 | evtMsgType | Message Type |  | enum16 |  |  | R | O | The number defining the meaning of the message. | See the Xtender seriál protocol appendix part messages.
enum16 | evtMsgType |  |  | Name: msg0; Label: Warning (000): Battery low; Value: 0
enum16 | evtMsgType |  |  | Name: msg1; Label: Warning (001): Battery too high; Value: 1
enum16 | evtMsgType |  |  | Name: msg2; Label: Warning (002): Bulk charge too long; Value: 2
enum16 | evtMsgType |  |  | Name: msg3; Label: (003): AC-In synchronization in progress; Value: 3
enum16 | evtMsgType |  |  | Name: msg4; Label: Warning (004): Input frequency AC-In wrong; Value: 4
enum16 | evtMsgType |  |  | Name: msg5; Label: Warning (005): Input frequency AC-In wrong; Value: 5
enum16 | evtMsgType |  |  | Name: msg6; Label: Warning (006): Input voltage AC-In too high; Value: 6
enum16 | evtMsgType |  |  | Name: msg7; Label: Warning (007): Input voltage AC-In too low; Value: 7
enum16 | evtMsgType |  |  | Name: msg8; Label: Halted (008): Inverter overload SC; Value: 8
enum16 | evtMsgType |  |  | Name: msg9; Label: Halted (009): Charger short circuit; Value: 9
enum16 | evtMsgType |  |  | Name: msg10; Label: (010): System start-up in progress; Value: 10
enum16 | evtMsgType |  |  | Name: msg11; Label: Warning (011): AC-In Energy quota; Value: 11
enum16 | evtMsgType |  |  | Name: msg12; Label: (012): Use of battery temperature sensor; Value: 12
enum16 | evtMsgType |  |  | Name: msg13; Label: (013): Use of additional remote control; Value: 13
enum16 | evtMsgType |  |  | Name: msg14; Label: Halted (014): Over temperature EL; Value: 14
enum16 | evtMsgType |  |  | Name: msg15; Label: Halted (015): Inverter overload BL; Value: 15
enum16 | evtMsgType |  |  | Name: msg16; Label: Warning (016): Fan error detected; Value: 16
enum16 | evtMsgType |  |  | Name: msg17; Label: (017): Programing mode; Value: 17
enum16 | evtMsgType |  |  | Name: msg18; Label: Warning (018): Excessive battery voltage ripple; Value: 18
enum16 | evtMsgType |  |  | Name: msg19; Label: Halted (019): Battery undervoltage; Value: 19
enum16 | evtMsgType |  |  | Name: msg20; Label: Halted (020): Battery overvoltage; Value: 20
enum16 | evtMsgType |  |  | Name: msg21; Label: (021): Transfer not authorized, AC-Out current is higher than {1107}; Value: 21
enum16 | evtMsgType |  |  | Name: msg22; Label: Halted (022): Voltage presence on AC-Out; Value: 22
enum16 | evtMsgType |  |  | Name: msg23; Label: Halted (023): Phase not defined; Value: 23
enum16 | evtMsgType |  |  | Name: msg24; Label: Warning (024): Change the clock battery; Value: 24
enum16 | evtMsgType |  |  | Name: msg25; Label: Halted (025): Unknown Command board. Software upgrade needed; Value: 25
enum16 | evtMsgType |  |  | Name: msg26; Label: Halted (026): Unknown Power board. Software upgrade needed; Value: 26
enum16 | evtMsgType |  |  | Name: msg27; Label: Halted (027): Unknown extension board. Software upgrade needed; Value: 27
enum16 | evtMsgType |  |  | Name: msg28; Label: Halted (028): Voltage incompatibility Power - Command; Value: 28
enum16 | evtMsgType |  |  | Name: msg29; Label: Halted (029): Voltage incompatibility Ext. - Command; Value: 29
enum16 | evtMsgType |  |  | Name: msg30; Label: Halted (030): Power incompatibility Power - Command; Value: 30
enum16 | evtMsgType |  |  | Name: msg31; Label: Halted (031): Command board software incompatibility; Value: 31
enum16 | evtMsgType |  |  | Name: msg32; Label: Halted (032): Power board software incompatibility; Value: 32
enum16 | evtMsgType |  |  | Name: msg33; Label: Halted (033): Extension board software incompatibility; Value: 33
enum16 | evtMsgType |  |  | Name: msg34; Label: Halted (034): FID corruption, call factory; Value: 34
enum16 | evtMsgType |  |  | Name: msg35; Label: (035): Memory structure modified; Value: 35
enum16 | evtMsgType |  |  | Name: msg36; Label: Halted (036): Parameter file lacking; Value: 36
enum16 | evtMsgType |  |  | Name: msg37; Label: Warning (037): Message file lack. SW upgrade advised; Value: 37
enum16 | evtMsgType |  |  | Name: msg38; Label: Warning (038): Upgrade of the device software advised; Value: 38
enum16 | evtMsgType |  |  | Name: msg39; Label: Warning (039): Upgrade of the device software advised; Value: 39
enum16 | evtMsgType |  |  | Name: msg40; Label: Warning (040): Upgrade of the device software advised; Value: 40
enum16 | evtMsgType |  |  | Name: msg41; Label: Warning (041): Over temperature TR; Value: 41
enum16 | evtMsgType |  |  | Name: msg42; Label: Halted (042): Unauthorized energy source at the output; Value: 42
enum16 | evtMsgType |  |  | Name: msg43; Label: (043): Start of monthly test; Value: 43
enum16 | evtMsgType |  |  | Name: msg44; Label: (044): End of successfully monthly test; Value: 44
enum16 | evtMsgType |  |  | Name: msg45; Label: Warning (045): Monthly autonomy test failed; Value: 45
enum16 | evtMsgType |  |  | Name: msg46; Label: (046): Start of weekly test; Value: 46
enum16 | evtMsgType |  |  | Name: msg47; Label: (047): End of successfully weekly test; Value: 47
enum16 | evtMsgType |  |  | Name: msg48; Label: Warning (048): Weekly autonomy test failed; Value: 48
enum16 | evtMsgType |  |  | Name: msg49; Label: (049): Transfer opened because AC-In max current exceeded {1107}; Value: 49
enum16 | evtMsgType |  |  | Name: msg50; Label: Error (050): Incomplete data transfer; Value: 50
enum16 | evtMsgType |  |  | Name: msg51; Label: (051): The update is finished; Value: 51
enum16 | evtMsgType |  |  | Name: msg52; Label: (052): Your installation is already updated; Value: 52
enum16 | evtMsgType |  |  | Name: msg53; Label: Halted (053): Devices not compatible, software update required; Value: 53
enum16 | evtMsgType |  |  | Name: msg54; Label: (054): Please wait. Data transfer in progress; Value: 54
enum16 | evtMsgType |  |  | Name: msg55; Label: Error (055): No SD card inserted; Value: 55
enum16 | evtMsgType |  |  | Name: msg56; Label: Warning (056): Upgrade of the RCC software advised; Value: 56
enum16 | evtMsgType |  |  | Name: msg57; Label: (057): Operation finished successfully; Value: 57
enum16 | evtMsgType |  |  | Name: msg58; Label: Halted (058): Master synchronization missing; Value: 58
enum16 | evtMsgType |  |  | Name: msg59; Label: Halted (059): Inverter overload HW; Value: 59
enum16 | evtMsgType |  |  | Name: msg60; Label: Warning (060): Time security 1512 AUX1; Value: 60
enum16 | evtMsgType |  |  | Name: msg61; Label: Warning (061): Time security 1513 AUX2; Value: 61
enum16 | evtMsgType |  |  | Name: msg62; Label: Warning (062): Genset, no AC-In coming after AUX command; Value: 62
enum16 | evtMsgType |  |  | Name: msg63; Label: (063): Save parameter XT; Value: 63
enum16 | evtMsgType |  |  | Name: msg64; Label: (064): Save parameter BSP; Value: 64
enum16 | evtMsgType |  |  | Name: msg65; Label: (065): Save parameter VarioTrack; Value: 65
enum16 | evtMsgType |  |  | Name: msg71; Label: Error (071): Insufficient disk space on SD card; Value: 71
enum16 | evtMsgType |  |  | Name: msg72; Label: Halted (072): COM identification incorrect; Value: 72
enum16 | evtMsgType |  |  | Name: msg73; Label: (073): Datalogger is enabled on this RCC; Value: 73
enum16 | evtMsgType |  |  | Name: msg74; Label: (074): Save parameter Xcom-MS; Value: 74
enum16 | evtMsgType |  |  | Name: msg75; Label: (075): MPPT MS address changed successfully; Value: 75
enum16 | evtMsgType |  |  | Name: msg76; Label: Error (076): Error during change of MPPT MS address; Value: 76
enum16 | evtMsgType |  |  | Name: msg77; Label: Error (077): Wrong MPPT MS DIP Switch position; Value: 77
enum16 | evtMsgType |  |  | Name: msg78; Label: (078): SMS or email sent; Value: 78
enum16 | evtMsgType |  |  | Name: msg79; Label: Halted (079): More than 9 XTs in the system; Value: 79
enum16 | evtMsgType |  |  | Name: msg80; Label: Halted (080): No battery (or reverse polarity); Value: 80
enum16 | evtMsgType |  |  | Name: msg81; Label: Warning (081): Earthing fault; Value: 81
enum16 | evtMsgType |  |  | Name: msg82; Label: Halted (082): PV overvoltage; Value: 82
enum16 | evtMsgType |  |  | Name: msg83; Label: Warning (083): No solar production in the last 48h; Value: 83
enum16 | evtMsgType |  |  | Name: msg84; Label: (084): Equalization performed; Value: 84
enum16 | evtMsgType |  |  | Name: msg85; Label: Error (085): Modem not available; Value: 85
enum16 | evtMsgType |  |  | Name: msg86; Label: Error (086): Incorrect PIN code, unable to initiate the modem; Value: 86
enum16 | evtMsgType |  |  | Name: msg87; Label: Error (087): Insufficient Signal from GSM modem; Value: 87
enum16 | evtMsgType |  |  | Name: msg88; Label: Error (088): No connection to GSM network; Value: 88
enum16 | evtMsgType |  |  | Name: msg89; Label: Error (089): No server access; Value: 89
enum16 | evtMsgType |  |  | Name: msg90; Label: (090): Server connected; Value: 90
enum16 | evtMsgType |  |  | Name: msg91; Label: Error (091): Update software of other RCC or Xcom-232i; Value: 91
enum16 | evtMsgType |  |  | Name: msg92; Label: Error (092): More than 3 RCC or Xcom-232i in the system; Value: 92
enum16 | evtMsgType |  |  | Name: msg93; Label: Error (093): More than 1 BSP in the system; Value: 93
enum16 | evtMsgType |  |  | Name: msg94; Label: Error (094): More than 1 Xcom-MS in the system; Value: 94
enum16 | evtMsgType |  |  | Name: msg95; Label: Error (095): More than 15 VarioTrack in the system; Value: 95
enum16 | evtMsgType |  |  | Name: msg121; Label: Error (121): Impossible communication with target device; Value: 121
enum16 | evtMsgType |  |  | Name: msg122; Label: Error (122): SD card corrupted; Value: 122
enum16 | evtMsgType |  |  | Name: msg123; Label: Error (123): SD card not formatted; Value: 123
enum16 | evtMsgType |  |  | Name: msg124; Label: Error (124): SD card not compatible; Value: 124
enum16 | evtMsgType |  |  | Name: msg125; Label: Error (125): SD card format not recognized. Should be FAT; Value: 125
enum16 | evtMsgType |  |  | Name: msg126; Label: Error (126): SD card write protected; Value: 126
enum16 | evtMsgType |  |  | Name: msg127; Label: Error (127): SD card, file(s) corrupted; Value: 127
enum16 | evtMsgType |  |  | Name: msg128; Label: Error (128): SD card file or directory could not be found; Value: 128
enum16 | evtMsgType |  |  | Name: msg129; Label: Error (129): SD card has been prematurely removed; Value: 129
enum16 | evtMsgType |  |  | Name: msg130; Label: Error (130): Update directory is empty; Value: 130
enum16 | evtMsgType |  |  | Name: msg131; Label: (131): The VarioTrack is configured for 12V batteries; Value: 131
enum16 | evtMsgType |  |  | Name: msg132; Label: (132): The VarioTrack is configured for 24V batteries; Value: 132
enum16 | evtMsgType |  |  | Name: msg133; Label: (133): The VarioTrack is configured for 48V batteries; Value: 133
enum16 | evtMsgType |  |  | Name: msg134; Label: (134): Reception level of the GSM signal; Value: 134
enum16 | evtMsgType |  |  | Name: msg137; Label: (137): VarioTrack master synchronization lost; Value: 137
enum16 | evtMsgType |  |  | Name: msg138; Label: Error (138): XT master synchronization lost; Value: 138
enum16 | evtMsgType |  |  | Name: msg139; Label: (139): Synchronized on VarioTrack master; Value: 139
enum16 | evtMsgType |  |  | Name: msg140; Label: (140): Synchronized on XT master; Value: 140
enum16 | evtMsgType |  |  | Name: msg141; Label: Error (141): More than 1 Xcom-SMS in the system; Value: 141
enum16 | evtMsgType |  |  | Name: msg142; Label: Error (142): More than 15 VarioString in the system; Value: 142
enum16 | evtMsgType |  |  | Name: msg143; Label: (143): Save parameter Xcom-SMS; Value: 143
enum16 | evtMsgType |  |  | Name: msg144; Label: (144): Save parameter VarioString; Value: 144
enum16 | evtMsgType |  |  | Name: msg145; Label: Error (145): SIM card blocked, PUK code required; Value: 145
enum16 | evtMsgType |  |  | Name: msg146; Label: Error (146): SIM card missing; Value: 146
enum16 | evtMsgType |  |  | Name: msg147; Label: Error (147): Install R532 firmware release prior to install an older release; Value: 147
enum16 | evtMsgType |  |  | Name: msg148; Label: (148): Datalogger function interrupted (SD card removed); Value: 148
enum16 | evtMsgType |  |  | Name: msg149; Label: Error (149): Parameter setting incomplete; Value: 149
enum16 | evtMsgType |  |  | Name: msg150; Label: Error (150): Cabling error between PV and VarioString; Value: 150
enum16 | evtMsgType |  |  | Name: msg162; Label: Error (162): Communication loss with RCC or Xcom-232i; Value: 162
enum16 | evtMsgType |  |  | Name: msg163; Label: Error (163): Communication loss with Xtender; Value: 163
enum16 | evtMsgType |  |  | Name: msg164; Label: Error (164): Communication loss with BSP; Value: 164
enum16 | evtMsgType |  |  | Name: msg165; Label: Error (165): Communication loss with Xcom-MS; Value: 165
enum16 | evtMsgType |  |  | Name: msg166; Label: Error (166): Communication loss with VarioTrack; Value: 166
enum16 | evtMsgType |  |  | Name: msg167; Label: Error (167): Communication loss with VarioString; Value: 167
enum16 | evtMsgType |  |  | Name: msg168; Label: (168): Synchronized with VarioString master; Value: 168
enum16 | evtMsgType |  |  | Name: msg169; Label: (169): Synchronization with VarioString master lost; Value: 169
enum16 | evtMsgType |  |  | Name: msg170; Label: Warning (170): No solar production in the last 48h on PV1; Value: 170
enum16 | evtMsgType |  |  | Name: msg171; Label: Warning (171): No solar production in the last 48h on PV2; Value: 171
enum16 | evtMsgType |  |  | Name: msg172; Label: Error (172): FID change impossible. More than one unit.; Value: 172
enum16 | evtMsgType |  |  | Name: msg173; Label: Error (173): Incompatible Xtender. Please contact Studer Innotec SA; Value: 173
enum16 | evtMsgType |  |  | Name: msg174; Label: (174): Inaccessible parameter, managed by the Xcom-CAN; Value: 174
enum16 | evtMsgType |  |  | Name: msg175; Label: Halted (175): Critical undervoltage; Value: 175
enum16 | evtMsgType |  |  | Name: msg176; Label: (176): Calibration setting lost; Value: 176
enum16 | evtMsgType |  |  | Name: msg177; Label: (177): An Xtender has started up; Value: 177
enum16 | evtMsgType |  |  | Name: msg178; Label: (178): No BSP. Necessary for programming with SOC; Value: 178
enum16 | evtMsgType |  |  | Name: msg179; Label: (179): No BTS or BSP. Necessary for programming with temperature; Value: 179
enum16 | evtMsgType |  |  | Name: msg180; Label: (180): Command entry activated; Value: 180
enum16 | evtMsgType |  |  | Name: msg181; Label: Error (181): Disconnection of BTS; Value: 181
enum16 | evtMsgType |  |  | Name: msg182; Label: (182): BTS/BSP battery temperature measurement used by a device; Value: 182
enum16 | evtMsgType |  |  | Name: msg183; Label: Halted (183): An Xtender has lost communication with the system; Value: 183
enum16 | evtMsgType |  |  | Name: msg184; Label: Error (184): Check phase orientation or circuit breakers state on AC-In; Value: 184
enum16 | evtMsgType |  |  | Name: msg185; Label: Warning (185): AC-In voltage level with delay too low; Value: 185
enum16 | evtMsgType |  |  | Name: msg186; Label: Halted (186): Critical undervoltage (fast); Value: 186
enum16 | evtMsgType |  |  | Name: msg187; Label: Halted (187): Critical overvoltage (fast); Value: 187
enum16 | evtMsgType |  |  | Name: msg188; Label: (188): CAN stage startup; Value: 188
enum16 | evtMsgType |  |  | Name: msg189; Label: Error (189): Incompatible configuration file; Value: 189
enum16 | evtMsgType |  |  | Name: msg190; Label: (190): The Xcom-SMS is busy; Value: 190
enum16 | evtMsgType |  |  | Name: msg191; Label: (191): Parameter not supported; Value: 191
enum16 | evtMsgType |  |  | Name: msg192; Label: (192): Unknown reference; Value: 192
enum16 | evtMsgType |  |  | Name: msg193; Label: (193): Invalid value; Value: 193
enum16 | evtMsgType |  |  | Name: msg194; Label: (194): Value too low; Value: 194
enum16 | evtMsgType |  |  | Name: msg195; Label: (195): Value too high; Value: 195
enum16 | evtMsgType |  |  | Name: msg196; Label: (196): Writing error; Value: 196
enum16 | evtMsgType |  |  | Name: msg197; Label: (197): Reading error; Value: 197
enum16 | evtMsgType |  |  | Name: msg198; Label: (198): User level insufficient; Value: 198
enum16 | evtMsgType |  |  | Name: msg199; Label: (199): No data for the report; Value: 199
enum16 | evtMsgType |  |  | Name: msg200; Label: Error (200): Memory full; Value: 200
enum16 | evtMsgType |  |  | Name: msg202; Label: Warning (202): External alarm arrives; Value: 202
enum16 | evtMsgType |  |  | Name: msg203; Label: (203): External alarm leaves; Value: 203
enum16 | evtMsgType |  |  | Name: msg204; Label: Error (204): External stop arrives; Value: 204
enum16 | evtMsgType |  |  | Name: msg205; Label: (205): External stop leaves; Value: 205
enum16 | evtMsgType |  |  | Name: msg206; Label: Halted (206): Board hardware incompatibility; Value: 206
enum16 | evtMsgType |  |  | Name: msg207; Label: (207): AUX1 relay activation; Value: 207
enum16 | evtMsgType |  |  | Name: msg208; Label: (208): AUX1 relay deactivation; Value: 208
enum16 | evtMsgType |  |  | Name: msg209; Label: (209): AUX2 relay activation; Value: 209
enum16 | evtMsgType |  |  | Name: msg210; Label: (210): AUX2 relay deactivation; Value: 210
enum16 | evtMsgType |  |  | Name: msg211; Label: (211): Command entry deactivated; Value: 211
enum16 | evtMsgType |  |  | Name: msg212; Label: Error (212): VarioTrack software incompatibility. Upgrade needed; Value: 212
enum16 | evtMsgType |  |  | Name: msg213; Label: (213): Battery current limitation by the BSP stopped; Value: 213
enum16 | evtMsgType |  |  | Name: msg214; Label: Warning (214): Half period RMS voltage limit exceeded, transfer opened; Value: 214
enum16 | evtMsgType |  |  | Name: msg215; Label: Warning (215): UPS limit reached, transfer opened; Value: 215
enum16 | evtMsgType |  |  | Name: msg216; Label: Warning (216): Scom watchdog caused the reset of Xcom-232i; Value: 216
enum16 | evtMsgType |  |  | Name: msg217; Label: Warning (217): CAN problem at Xtender declaration; Value: 217
enum16 | evtMsgType |  |  | Name: msg218; Label: Warning (218): CAN problem while writing parameters; Value: 218
enum16 | evtMsgType |  |  | Name: msg222; Label: (222): Front ON/OFF button pressed; Value: 222
enum16 | evtMsgType |  |  | Name: msg223; Label: (223): Main OFF detected; Value: 223
enum16 | evtMsgType |  |  | Name: msg224; Label: (224): Delay before closing transfer relay in progress {1580}; Value: 224
enum16 | evtMsgType |  |  | Name: msg225; Label: Error (225): Communication with lithium battery lost; Value: 225
enum16 | evtMsgType |  |  | Name: msg226; Label: (226): Communication with lithium battery restored; Value: 226

## 64410
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer Xtender Model | 64410 | uint16 |  |  | R | M | Studer-Innotec Xtender Model
Header |  | 1 |  | 1 | L |  | 98 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | xtModel | XT Model |  | string |  |  | R | O | 3124-3125
Fixed Block |  | 18 | 16 | 16 | xtFID | XT FID |  | string |  |  | R | O | 3056-3057
Fixed Block |  | 34 | 32 | 16 | xtSwVersion | Software Version |  | string |  |  | R | O | 3030-3031
Fixed Block |  | 50 | 48 | 2 | xtIdBatteryVoltage | ID Battery Voltage |  | float32 |  |  | R | O | 3127
Fixed Block |  | 52 | 50 | 2 | xtDefinedPhase | Defined Phase |  | float32 |  |  | R | O | 3089
Fixed Block |  | 54 | 52 | 1 | xtState | State |  | enum16 |  |  | R | O | 3049
Fixed Block |  | 55 | 53 | 2 | xtBatteryVoltage | Battery Voltage |  | float32 |  |  | R | O | 3092
Fixed Block |  | 57 | 55 | 2 | xtBatteryChargeCurrent | Battery Charge Current |  | float32 |  |  | R | O | 3095
Fixed Block |  | 59 | 57 | 1 | xtBatteryCyclePhase | Battery Cycle Current |  | enum16 |  |  | R | O | 3010
Fixed Block |  | 60 | 58 | 2 | xtInVoltage | Input Voltage |  | float32 |  |  | R | O | 3113
Fixed Block |  | 62 | 60 | 2 | xtInVoltageMin | Input Voltage Min |  | float32 |  |  | R | O | 3111
Fixed Block |  | 64 | 62 | 2 | xtInVoltageMax | Input Voltage Max |  | float32 |  |  | R | O | 3112
Fixed Block |  | 66 | 64 | 2 | xtInCurrent | Input Current |  | float32 |  |  | R | O | 3116
Fixed Block |  | 68 | 66 | 2 | xtInCurrentMin | Input Current Min |  | float32 |  |  | R | O | 3114
Fixed Block |  | 70 | 68 | 2 | xtInCurrentMax | Input Current Max |  | float32 |  |  | R | O | 3115
Fixed Block |  | 72 | 70 | 2 | xtInFrequency | Input Frequency |  | float32 |  |  | R | O | 3122
Fixed Block |  | 74 | 72 | 2 | xtInFrequencyMin | Input Frequency Min |  | float32 |  |  | R | O | 3120
Fixed Block |  | 76 | 74 | 2 | xtInFrequencyMax | Input Frequency Max |  | float32 |  |  | R | O | 3121
Fixed Block |  | 78 | 76 | 2 | xtInApparentPower | Input Apparent Power |  | float32 |  |  | R | O | 3138
Fixed Block |  | 80 | 78 | 2 | xtInActivePower | Input Active Power |  | float32 |  |  | R | O | 3119
Fixed Block |  | 82 | 80 | 2 | xtOutVoltage | Output Voltage |  | float32 |  |  | R | O | 3021
Fixed Block |  | 84 | 82 | 2 | xtOutCurrent | Output Current |  | float32 |  |  | R | O | 3022
Fixed Block |  | 86 | 84 | 2 | xtOutFrequency | Output Frequency |  | float32 |  |  | R | O | 3110
Fixed Block |  | 88 | 86 | 2 | xtOutApparentPower | Output Apparent Power |  | float32 |  |  | R | O | 3139
Fixed Block |  | 90 | 88 | 2 | xtOutActivePower | Output Active Power |  | float32 |  |  | R | O | 3101
Fixed Block |  | 92 | 90 | 1 | xtOperatingState | Operating State |  | enum16 |  |  | R | O
Fixed Block |  | 93 | 91 | 1 | xtTransferRelay | State of Transfer Relay |  | enum16 |  |  | R | O | 3020
Fixed Block |  | 94 | 92 | 1 | xtRemoteEntryState | Remote Entry State |  | enum16 |  |  | R | O | 3086
Fixed Block |  | 95 | 93 | 1 | xtBatteryPriorityActive | Battery Priority Active |  | uint16 |  |  | R | O | 3161
Fixed Block |  | 96 | 94 | 1 | xtAUX1RelayState | State of Auxillary Relay 1 |  | enum16 |  |  | R | O | 3031
Fixed Block |  | 97 | 95 | 1 | xtAUX1RelayMode | Relay AUX 1 Mode |  | enum16 |  |  | R | O | 3054
Fixed Block |  | 98 | 96 | 1 | xtAUX2RelayState | State of Auxillary Relay 2 |  | enum16 |  |  | R | O | 3032
Fixed Block |  | 99 | 97 | 1 | xtAUX2RelayMode | Relay AUX 2 Mode |  | enum16 |  |  | R | O | 3055
enum16 | xtState |  |  | Name: off; Label: Offline; Value: 0
enum16 | xtState |  |  | Name: on; Label: Online; Value: 1
enum16 | xtBatteryCyclePhase |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtBatteryCyclePhase |  |  | Name: bulk; Label: Bulk; Value: 1
enum16 | xtBatteryCyclePhase |  |  | Name: absorption; Label: Absorption; Value: 2
enum16 | xtBatteryCyclePhase |  |  | Name: equalise; Label: Equalise; Value: 3
enum16 | xtBatteryCyclePhase |  |  | Name: floating; Label: Floating; Value: 4
enum16 | xtBatteryCyclePhase |  |  | Name: rFloating; Label: R Floating; Value: 5
enum16 | xtBatteryCyclePhase |  |  | Name: perAbsorption; Label: Per Absorption; Value: 6
enum16 | xtBatteryCyclePhase |  |  | Name: mixing; Label: Mixing; Value: 7
enum16 | xtBatteryCyclePhase |  |  | Name: forming; Label: Forming; Value: 8
enum16 | xtOperatingState |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtOperatingState |  |  | Name: inverter; Label: Inverter; Value: 1
enum16 | xtOperatingState |  |  | Name: charger; Label: Charger; Value: 2
enum16 | xtOperatingState |  |  | Name: boost; Label: Boost; Value: 3
enum16 | xtOperatingState |  |  | Name: injection; Label: Injection; Value: 4
enum16 | xtTransferRelay |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtTransferRelay |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtRemoteEntryState |  |  | Name: rmEn0; Label: Remote Entry 0; Value: 0
enum16 | xtRemoteEntryState |  |  | Name: rmEn1; Label: Remote Entry 1; Value: 1
enum16 | xtAUX1RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtAUX1RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtAUX1RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtAUX1RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | xtAUX1RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | xtAUX1RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | xtAUX1RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | xtAUX1RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | xtAUX2RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | xtAUX2RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | xtAUX2RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | xtAUX2RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | xtAUX2RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | xtAUX2RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | xtAUX2RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | xtAUX2RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5

## 64411
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer VarioTrack Model | 64411 | uint16 |  |  | R | M | Studer-Innotec VarioTrack Model
Header |  | 1 |  | 1 | L |  | 73 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | vtModel | VT Model |  | string |  |  | R | O | 11015
Fixed Block |  | 18 | 16 | 16 | vtFID | VT FID |  | string |  |  | R | O | 11067-11068
Fixed Block |  | 34 | 32 | 16 | vtSwVersion | Software Version |  | string |  |  | R | O | 11050-11051
Fixed Block |  | 50 | 48 | 2 | vtBatteryNominalVoltage | Battery Nominal Voltage |  | float32 |  |  | R | O | 11048
Fixed Block |  | 52 | 50 | 1 | vtState | State |  | enum16 |  |  | R | O | 11069
Fixed Block |  | 53 | 51 | 1 | vtErrType | Error Type |  | enum16 |  |  | R | O | 11034
Fixed Block |  | 54 | 52 | 2 | vtBatteryVoltage | Battery Voltage |  | float32 |  |  | R | O | 11000
Fixed Block |  | 56 | 54 | 2 | vtBatteryCurrent | Battery Current |  | float32 |  |  | R | O | 11001
Fixed Block |  | 58 | 56 | 1 | vtBatteryCyclePhase | Battery Cycle Phase |  | enum16 |  |  | R | O | 11038
Fixed Block |  | 59 | 57 | 1 | vtSynState | Synchronization State |  | enum16 |  |  | R | O | 11066
Fixed Block |  | 60 | 58 | 2 | vtPVGenVol | Voltage of the PV generator |  | float32 |  |  | R | O | 11002
Fixed Block |  | 62 | 60 | 2 | vtPVGenPow | Power of the PV generator |  | float32 |  |  | R | O | 11004
Fixed Block |  | 64 | 62 | 2 | vtBatteryTemp | Battery Temperature |  | float32 |  |  | R | O | 11005; Only if BTS-01 or BSP present
Fixed Block |  | 66 | 64 | 1 | vtOperatingMode | Operating Mode |  | enum16 |  |  | R | O | 11016
Fixed Block |  | 67 | 65 | 1 | vtAUX1RelayState | State of Auxillary Relay 1 |  | enum16 |  |  | R | O | 11061
Fixed Block |  | 68 | 66 | 1 | vtAUX1RelayMode | Relay AUX 1 Mode |  | enum16 |  |  | R | O | 11063
Fixed Block |  | 69 | 67 | 1 | vtAUX2RelayState | State of Auxillary Relay 2 |  | enum16 |  |  | R | O | 11062
Fixed Block |  | 70 | 68 | 1 | vtAUX2RelayMode | Relay AUX 2 Mode |  | enum16 |  |  | R | O | 11064
Fixed Block |  | 71 | 69 | 1 | vtAUX3RelayState | State of Auxillary Relay 3 |  | enum16 |  |  | R | O | 11077
Fixed Block |  | 72 | 70 | 1 | vtAUX3RelayMode | Relay AUX 3 Mode |  | enum16 |  |  | R | O | 11079
Fixed Block |  | 73 | 71 | 1 | vtAUX4RelayState | State of Auxillary Relay 4 |  | enum16 |  |  | R | O | 11078
Fixed Block |  | 74 | 72 | 1 | vtAUX4RelayMode | Relay AUX 4 Mode |  | enum16 |  |  | R | O | 11080
enum16 | vtState |  |  | Name: off; Label: Offline; Value: 6
enum16 | vtState |  |  | Name: on; Label: Online; Value: 1
enum16 | vtErrType |  |  | Name: noError; Label: No Error; Value: 0
enum16 | vtErrType |  |  | Name: batteryOverVoltage; Label: Battery Over Voltage; Value: 5
enum16 | vtErrType |  |  | Name: earth; Label: Earth; Value: 2
enum16 | vtErrType |  |  | Name: noBattery; Label: No Battery; Value: 3
enum16 | vtErrType |  |  | Name: overTemperature; Label: Over Temperature; Value: 4
enum16 | vtErrType |  |  | Name: pvOverVoltage; Label: PV Over Voltage; Value: 6
enum16 | vtErrType |  |  | Name: others; Label: Others; Value: 7
enum16 | vtErrType |  |  | Name: driv12Voltage; Label: Driv 12 Voltage; Value: 8
enum16 | vtErrType |  |  | Name: underCurrent; Label: Under Current; Value: 9
enum16 | vtErrType |  |  | Name: int12Voltage; Label: Int 12 Voltage; Value: 10
enum16 | vtErrType |  |  | Name: overCurrent; Label: Over Current; Value: 11
enum16 | vtErrType |  |  | Name: hardError; Label: Hard Error; Value: 12
enum16 | vtBatteryCyclePhase |  |  | Name: bulk; Label: Bulk; Value: 0
enum16 | vtBatteryCyclePhase |  |  | Name: absorption; Label: Absorption; Value: 1
enum16 | vtBatteryCyclePhase |  |  | Name: equalize; Label: Equalize; Value: 2
enum16 | vtBatteryCyclePhase |  |  | Name: floating; Label: Floating; Value: 3
enum16 | vtBatteryCyclePhase |  |  | Name: xtSlave; Label: XTender Slave; Value: 4
enum16 | vtBatteryCyclePhase |  |  | Name: vtSlave; Label: VarioTrack Slave; Value: 5
enum16 | vtBatteryCyclePhase |  |  | Name: rFloating; Label: R Floating; Value: 6
enum16 | vtBatteryCyclePhase |  |  | Name: perAbsorption; Label: Per Absorption; Value: 7
enum16 | vtSynState |  |  | Name: xtSlave; Label: XTender Slave; Value: 4
enum16 | vtSynState |  |  | Name: vtSlave; Label: VarioTrack Slave; Value: 5
enum16 | vtSynState |  |  | Name: vtMaster; Label: VarioTrack Master; Value: 8
enum16 | vtSynState |  |  | Name: autonomy; Label: Autonomy; Value: 9
enum16 | vtSynState |  |  | Name: vsSlave; Label: VarioString Slave; Value: 10
enum16 | vtSynState |  |  | Name: vsMaster; Label: VarioString Master; Value: 11
enum16 | vtOperatingMode |  |  | Name: night; Label: Night; Value: 0
enum16 | vtOperatingMode |  |  | Name: startUp; Label: Start Up; Value: 1
enum16 | vtOperatingMode |  |  | Name: scanning; Label: Scanning; Value: 2
enum16 | vtOperatingMode |  |  | Name: charger; Label: Charger; Value: 3
enum16 | vtOperatingMode |  |  | Name: manual; Label: Manual; Value: 4
enum16 | vtOperatingMode |  |  | Name: security; Label: Security; Value: 5
enum16 | vtOperatingMode |  |  | Name: off; Label: Offline; Value: 6
enum16 | vtOperatingMode |  |  | Name: slave; Label: Slave; Value: 7
enum16 | vtOperatingMode |  |  | Name: charge; Label: Charge; Value: 8
enum16 | vtOperatingMode |  |  | Name: chargeVoltage; Label: Charge Voltage; Value: 9
enum16 | vtOperatingMode |  |  | Name: chargeCurrent; Label: Charge Current; Value: 10
enum16 | vtOperatingMode |  |  | Name: chargeTemperature; Label: Charge Temperature; Value: 11
enum16 | vtAUX1RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vtAUX1RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vtAUX1RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vtAUX1RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vtAUX1RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vtAUX1RelayMode |  |  | Name: manualOn; Label: Manual; Value: 3
enum16 | vtAUX1RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vtAUX1RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | vtAUX2RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vtAUX2RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vtAUX2RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vtAUX2RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vtAUX2RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vtAUX2RelayMode |  |  | Name: manualOn; Label: Manual; Value: 3
enum16 | vtAUX2RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vtAUX2RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | vtAUX3RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vtAUX3RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vtAUX3RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vtAUX3RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vtAUX3RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vtAUX3RelayMode |  |  | Name: manualOn; Label: Manual; Value: 3
enum16 | vtAUX3RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vtAUX3RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | vtAUX4RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vtAUX4RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vtAUX4RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vtAUX4RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vtAUX4RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vtAUX4RelayMode |  |  | Name: manualOn; Label: Manual; Value: 3
enum16 | vtAUX4RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vtAUX4RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5

## 64412
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer VarioString Model | 64412 | uint16 |  |  | R | M | Studer-Innotec VarioString Model
Header |  | 1 |  | 1 | L |  | 90 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | vsModel | VS Model |  | string |  |  | R | O | 15074
Fixed Block |  | 18 | 16 | 16 | vsFID | VS FID |  | string |  |  | R | O | 15102-15103
Fixed Block |  | 34 | 32 | 16 | vsSwVersion | Software Version |  | string |  |  | R | O | 15077-15078
Fixed Block |  | 50 | 48 | 1 | vsState | State |  | enum16 |  |  | R | O | 15108
Fixed Block |  | 51 | 49 | 1 | vsErrType | Error Type |  | enum16 |  |  | R | O | 15049
Fixed Block |  | 52 | 50 | 2 | vsBatteryTemp | Battery Temperature |  | float32 |  |  | R | O | 15032
Fixed Block |  | 54 | 52 | 1 | vsBatteryCyclePhase | Battery Cycle Phase |  | enum16 |  |  | R | O | 15002
Fixed Block |  | 55 | 53 | 2 | vsBatteryVoltage | Battery Voltage |  | float32 |  |  | R | O | 15000
Fixed Block |  | 57 | 55 | 2 | vsBatteryCurrent | Battery Current |  | float32 |  |  | R | O | 15001
Fixed Block |  | 59 | 57 | 1 | vsSynState | Synchronization State |  | enum16 |  |  | R | O | 15051
Fixed Block |  | 60 | 58 | 1 | vsPVWiringType | PV Type of Wiring |  | enum16 |  |  | R | O | 15003
Fixed Block |  | 61 | 59 | 2 | vsPVPower | PV Power |  | float32 |  |  | R | O | if {15003}=2 or 3 then {15010};if Model=VS-70, use only this value, if Model=VS-120, use {15010}if wiring is 'series' or 'parallel'
Fixed Block |  | 63 | 61 | 2 | vsPV1Power | PV Power 1 |  | float32 |  |  | R | O | if {15003}=1 then {15011};Only if Model=VS-120 and wiring is 'independent' use {15011}, else no value
Fixed Block |  | 65 | 63 | 2 | vsPV2Power | PV Power 2 |  | float32 |  |  | R | O | if {15012}=1 then {15012};Only if Model=VS-120 and wiring is 'independent' use {15012}, else no value
Fixed Block |  | 67 | 65 | 2 | vsPVVoltage | PV Voltage |  | float32 |  |  | R | O | if {15003}=2 or 3 then {15004};if Model=VS-70, use only this value, if Model=VS-120, use this value if wiring is 'series' or 'parallel'
Fixed Block |  | 69 | 67 | 2 | vsPV1Voltage | PV Voltage 1 |  | float32 |  |  | R | O | if {15003}=1 then {15005};Only if Model=VS-120 and wiring is 'independent' use {15005}, else no value
Fixed Block |  | 71 | 69 | 2 | vsPV2Voltage | PV Voltage 2 |  | float32 |  |  | R | O | if {15003}=1 then {15006};Only if Model=VS-120 and wiring is 'independent' use {15006}, else no value
Fixed Block |  | 73 | 71 | 2 | vsPVCurrent | PV Current |  | float32 |  |  | R | O | 15007
Fixed Block |  | 75 | 73 | 2 | vsPV1Current | PV Current 1 |  | float32 |  |  | R | O | 15008
Fixed Block |  | 77 | 75 | 2 | vsPV2Current | PV Current 2 |  | float32 |  |  | R | O | 15009
Fixed Block |  | 79 | 77 | 2 | vsPVProducedEnergy | PV Produced Energy |  | float32 |  |  | R | O | 15017
Fixed Block |  | 81 | 79 | 2 | vsPV1ProducedEnergy | PV Produced Energy 1 |  | float32 |  |  | R | O | 15018
Fixed Block |  | 83 | 81 | 2 | vsPV2ProducedEnergy | PV Produced Energy 2 |  | float32 |  |  | R | O | 15019
Fixed Block |  | 85 | 83 | 1 | vsPVOperatingMode | PV Operating Mode |  | enum16 |  |  | R | O | 15013
Fixed Block |  | 86 | 84 | 1 | vsPV1OperatingMode | PV 1 Operating Mode |  | enum16 |  |  | R | O | 15014
Fixed Block |  | 87 | 85 | 1 | vsPV2OperatingMode | PV 2 Operating Mode |  | enum16 |  |  | R | O | 15015
Fixed Block |  | 88 | 86 | 1 | vsAUX1RelayState | State of Auxillary Aux 1 |  | enum16 |  |  | R | O | 15088
Fixed Block |  | 89 | 87 | 1 | vsAUX1RelayMode | Relay Aux 1 Mode |  | enum16 |  |  | R | O | 15090
Fixed Block |  | 90 | 88 | 1 | vsAUX2RelayState | State of Auxillary Aux 2 |  | enum16 |  |  | R | O | 15089
Fixed Block |  | 91 | 89 | 1 | vsAUX2RelayMode | Relay Aux 2 Mode |  | enum16 |  |  | R | O | 15091
enum16 | vsState |  |  | Name: off; Label: Offline; Value: 2
enum16 | vsState |  |  | Name: on; Label: Online; Value: 1
enum16 | vsErrType |  |  | Name: none; Label: None; Value: 0
enum16 | vsErrType |  |  | Name: overVoltageBattery; Label: Over Voltage Battery; Value: 1
enum16 | vsErrType |  |  | Name: overVoltagePV; Label: Over Voltage PV; Value: 2
enum16 | vsErrType |  |  | Name: overVoltagePV1; Label: Over Voltage PV 1; Value: 3
enum16 | vsErrType |  |  | Name: overVoltagePV2; Label: Over Voltage PV 2; Value: 4
enum16 | vsErrType |  |  | Name: overCurrentPV; Label: Over Current PV; Value: 5
enum16 | vsErrType |  |  | Name: overCurrentPV1; Label: Over Current PV 1; Value: 6
enum16 | vsErrType |  |  | Name: overCurrentPV2; Label: Over Current PV 2; Value: 7
enum16 | vsErrType |  |  | Name: groundBattery; Label: Ground Battery; Value: 8
enum16 | vsErrType |  |  | Name: groundPV; Label: Ground PV; Value: 9
enum16 | vsErrType |  |  | Name: groundPV1; Label: Ground PV 1; Value: 10
enum16 | vsErrType |  |  | Name: groundPV2; Label: Ground PV 2; Value: 11
enum16 | vsErrType |  |  | Name: overTemperature; Label: Over Temperature; Value: 12
enum16 | vsErrType |  |  | Name: underVoltageBattery; Label: under Voltage Battery; Value: 13
enum16 | vsErrType |  |  | Name: cabling; Label: Cabling; Value: 14
enum16 | vsErrType |  |  | Name: other; Label: Other; Value: 15
enum16 | vsBatteryCyclePhase |  |  | Name: bulk; Label: Bulk; Value: 0
enum16 | vsBatteryCyclePhase |  |  | Name: absorption; Label: Absorption; Value: 1
enum16 | vsBatteryCyclePhase |  |  | Name: equalize; Label: Equalize; Value: 2
enum16 | vsBatteryCyclePhase |  |  | Name: floating; Label: Floating; Value: 3
enum16 | vsBatteryCyclePhase |  |  | Name: rFloating; Label: R Floating; Value: 6
enum16 | vsBatteryCyclePhase |  |  | Name: perAbsorption; Label: Per Absorption; Value: 7
enum16 | vsSynState |  |  | Name: xtSlave; Label: XTender Slave; Value: 4
enum16 | vsSynState |  |  | Name: vtSlave; Label: VarioTrack Slave; Value: 5
enum16 | vsSynState |  |  | Name: vtMaster; Label: VarioTrack Master; Value: 8
enum16 | vsSynState |  |  | Name: autonomy; Label: Autonomy; Value: 9
enum16 | vsSynState |  |  | Name: vsSlave; Label: VarioString Slave; Value: 10
enum16 | vsSynState |  |  | Name: vsMaster; Label: VarioString Master; Value: 11
enum16 | vsPVWiringType |  |  | Name: unknown; Label: Unknown; Value: 0
enum16 | vsPVWiringType |  |  | Name: independent; Label: Independent; Value: 1
enum16 | vsPVWiringType |  |  | Name: series; Label: Series; Value: 2
enum16 | vsPVWiringType |  |  | Name: parallel; Label: Parallel; Value: 3
enum16 | vsPVWiringType |  |  | Name: error; Label: Error; Value: 4
enum16 | vsPVOperatingMode |  |  | Name: night; Label: Night; Value: 0
enum16 | vsPVOperatingMode |  |  | Name: security; Label: Security; Value: 1
enum16 | vsPVOperatingMode |  |  | Name: off; Label: Offline; Value: 2
enum16 | vsPVOperatingMode |  |  | Name: charge; Label: Charge; Value: 3
enum16 | vsPVOperatingMode |  |  | Name: chargeVoltage; Label: Charge Voltage; Value: 4
enum16 | vsPVOperatingMode |  |  | Name: chargeCurrent; Label: Charge Current; Value: 5
enum16 | vsPVOperatingMode |  |  | Name: chargePower; Label: Charge Power; Value: 6
enum16 | vsPVOperatingMode |  |  | Name: chargeCurrentPV; Label: Charge Current PV; Value: 7
enum16 | vsPVOperatingMode |  |  | Name: chargeTemperature; Label: Charge Temperature; Value: 8
enum16 | vsPVOperatingMode |  |  | Name: chargeCurrentBSP; Label: Charge Current BSP; Value: 10
enum16 | vsPV1OperatingMode |  |  | Name: night; Label: Night; Value: 0
enum16 | vsPV1OperatingMode |  |  | Name: security; Label: Security; Value: 1
enum16 | vsPV1OperatingMode |  |  | Name: off; Label: Offline; Value: 2
enum16 | vsPV1OperatingMode |  |  | Name: charge; Label: Charge; Value: 3
enum16 | vsPV1OperatingMode |  |  | Name: chargeVoltage; Label: Charge Voltage; Value: 4
enum16 | vsPV1OperatingMode |  |  | Name: chargeCurrent; Label: Charge Current; Value: 5
enum16 | vsPV1OperatingMode |  |  | Name: chargePower; Label: Charge Power; Value: 6
enum16 | vsPV1OperatingMode |  |  | Name: chargeCurrentPV; Label: Charge Current PV; Value: 7
enum16 | vsPV1OperatingMode |  |  | Name: chargeTemperature; Label: Charge Temperature; Value: 8
enum16 | vsPV1OperatingMode |  |  | Name: chargeCurrentBSP; Label: Charge Current BSP; Value: 10
enum16 | vsPV2OperatingMode |  |  | Name: night; Label: Night; Value: 0
enum16 | vsPV2OperatingMode |  |  | Name: security; Label: Security; Value: 1
enum16 | vsPV2OperatingMode |  |  | Name: off; Label: Offline; Value: 2
enum16 | vsPV2OperatingMode |  |  | Name: charge; Label: Charge; Value: 3
enum16 | vsPV2OperatingMode |  |  | Name: chargeVoltage; Label: Charge Voltage; Value: 4
enum16 | vsPV2OperatingMode |  |  | Name: chargeCurrent; Label: Charge Current; Value: 5
enum16 | vsPV2OperatingMode |  |  | Name: chargePower; Label: Charge Power; Value: 6
enum16 | vsPV2OperatingMode |  |  | Name: chargeCurrentPV; Label: Charge Current PV; Value: 7
enum16 | vsPV2OperatingMode |  |  | Name: chargeTemperature; Label: Charge Temperature; Value: 8
enum16 | vsPV2OperatingMode |  |  | Name: chargeCurrentBSP; Label: Charge Current BSP; Value: 10
enum16 | vsAUX1RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vsAUX1RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vsAUX1RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vsAUX1RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vsAUX1RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vsAUX1RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | vsAUX1RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vsAUX1RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5
enum16 | vsAUX2RelayState |  |  | Name: opened; Label: Opened; Value: 0
enum16 | vsAUX2RelayState |  |  | Name: closed; Label: Closed; Value: 1
enum16 | vsAUX2RelayMode |  |  | Name: invalidValue; Label: Invalid Value; Value: 0
enum16 | vsAUX2RelayMode |  |  | Name: automatic; Label: Automatic; Value: 1
enum16 | vsAUX2RelayMode |  |  | Name: reversedAutomatic; Label: Reversed Automatic; Value: 2
enum16 | vsAUX2RelayMode |  |  | Name: manualOn; Label: Manual On; Value: 3
enum16 | vsAUX2RelayMode |  |  | Name: manualOff; Label: Manual Off; Value: 4
enum16 | vsAUX2RelayMode |  |  | Name: coupledForGeneratorStart; Label: Generator Start; Value: 5

## 64413
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Studer BSP Model | 64413 | uint16 |  |  | R | M | Studer-Innotec Battery Status Processor Model
Header |  | 1 |  | 1 | L |  | 64 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | bspModel | BSP Model |  | string |  |  | R | O | 7034
Fixed Block |  | 18 | 16 | 16 | bspFID | BSP FID |  | string |  |  | R | O | 7048-7049
Fixed Block |  | 34 | 32 | 16 | bspSwVersion | Software Version |  | string |  |  | R | O | 7037-7038
Fixed Block |  | 50 | 48 | 2 | bspBatteryVoltage | Battery Voltage |  | float32 |  |  | R | O | 7030
Fixed Block |  | 52 | 50 | 2 | bspBatteryCurrent | Battery Current |  | float32 |  |  | R | O | 7031
Fixed Block |  | 54 | 52 | 2 | bspStateOfCharge | State Of Charge |  | float32 |  |  | R | O | 7002
Fixed Block |  | 56 | 54 | 2 | bspPower | BSP Power |  | float32 |  |  | R | O | 7003
Fixed Block |  | 58 | 56 | 2 | bspBatteryTemp | Battery Temperature |  | float32 |  |  | R | O | 7029
Fixed Block |  | 60 | 58 | 2 | bspRemainingAutonomy | Remaining Autonomy |  | float32 |  |  | R | O | 7004
Fixed Block |  | 62 | 60 | 2 | bspAhChargedToday | Charged Today |  | float32 |  |  | R | O | 7007
Fixed Block |  | 64 | 62 | 2 | bspAhDischargedToday | Discharge Today |  | float32 |  |  | R | O | 7008

## 64420
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | 3 Phase Hybrid Inverter Model | 113 | uint16 |  |  | R | M | Include this model for three phase hybrid inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | Pac 1 grid | Power Grid Phase 1 |  | float32 | W |  | R | M | Active Power Grid Phase 1
Fixed Block |  | 4 | 2 | 2 | Pac 2 grid | Power Grid Phase 2 |  | float32 | W |  | R | M | Active Power Grid Phase 2
Fixed Block |  | 6 | 4 | 2 | Pac 3 grid | Power Grid Phase 3 |  | float32 | W |  | R | M | Active Power Grid Phase 3
Fixed Block |  | 8 | 6 | 2 | Pac grid | Power Grid |  | float32 | W |  | R | M | Active Power Grid | Sum of all phases
Fixed Block |  | 10 | 8 | 2 | Pac 1 load | Power Load Phase 1 |  | float32 | W |  | R | M | Active Power Load Phase 1
Fixed Block |  | 12 | 10 | 2 | Pac 2 load | Power Load Phase 2 |  | float32 | W |  | R | M | Active Power Load Phase 2
Fixed Block |  | 14 | 12 | 2 | Pac 3 load | Power Load Phase 3 |  | float32 | W |  | R | M | Active Power Load Phase 3
Fixed Block |  | 16 | 14 | 2 | Pac load | Power Load |  | float32 | W |  | R | M | Active Power Load | Sum of all phases
Fixed Block |  | 18 | 16 | 2 | Pac Backup R | Power Backup Phase R |  | float32 | W |  | R | M | Active Power Backup Phase R
Fixed Block |  | 20 | 18 | 2 | Pac Backup S | Power Backup Phase S |  | float32 | W |  | R | M | Active Power Backup Phase S
Fixed Block |  | 22 | 20 | 2 | Pac Backup T | Power Backup Phase T |  | float32 | W |  | R | M | Active Power Backup Phase T
Fixed Block |  | 24 | 22 | 2 | Pac Backup | Power Backup |  | float32 | W |  | R | M | Active Power Backup | Sum of all phases
Fixed Block |  | 26 | 24 | 1 | State | State |  | enum16 |  |  | R | O | Enumerated value. Operating state
enum16 | State |  |  | Name: WAITING; Label: Waiting; Units: 0 |  | Waiting / Idle
enum16 | State |  |  | Name: ONGRID; Label: OnGrid; Units: 1 |  | Connected to grid
enum16 | State |  |  | Name: OFFGRID; Label: OffGrid; Units: 2 |  | Disconnected from grid
enum16 | State |  |  | Name: FAULT; Label: Fault; Units: 3 |  | Inverter fault
enum16 | State |  |  | Name: FLASH; Label: Flash Update; Units: 4 |  | Flash / Firmware Update
enum16 | State |  |  | Name: CHECK; Label: PowerOnSelfCheck; Units: 5 |  | Power On self check

## 64500
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Description | Notes
Header |  | 0 |  | 1 | ID | Counter Model | 64500 | uint16 |  |  | R | Include this model for energy counter monitoring
Header |  | 1 |  | 1 | L |  | 3 + (Counter Count * 20) | uint16 |  |  | R | Model Length
Fixed Block |  | 2 | 0 | 2 | RunTime | Time |  | float32 | s |  | R | System Time since powerup in seconds
Fixed Block |  | 4 | 2 | 1 | N | Counter Count |  | uint16 |  |  | R | Number of Counter Repeating blocks
Repeating Block |  | 5 | 0 | 1 | ID | Counter ID |  | uint16 |  |  | R | Counter ID
Repeating Block |  | 6 | 1 | 11 | Name | Counter Name |  | string |  |  | R | Counter Name from SM2 Counter Settings
Repeating Block |  | 17 | 12 | 2 | Today | Today Wh/m3 |  | float32 | Wh / m3 |  | R | Today Energy/Volume (Wh/m3)
Repeating Block |  | 19 | 14 | 2 | Total | Total Wh/m3 |  | float32 | Wh / m3 |  | R | Total Energy/Volume (Wh/m3)
Repeating Block |  | 21 | 16 | 2 | P/Q | Power/FlowRate |  | float32 | W / l/h |  | R | Immediate Power or Flowrate (W / l/h)
Repeating Block |  | 23 | 18 | 1 | CtType | Counter Type |  | enum16 |  |  | R | Type of the counter
Repeating Block |  | 24 | 19 | 1 | CtUnit | Counter Unit |  | enum16 |  |  | R | Unit of the Total value (Wh/m3)
enum16 | CtType |  |  | Name: Electrometer Production; Label: Production from Electrometer; Value: 0
enum16 | CtType |  |  | Name: Electrometer Consumption; Label: Consumption from Electrometer; Value: 1
enum16 | CtType |  |  | Name: Electrometer Supply DS; Label: Supply to DS; Value: 2
enum16 | CtType |  |  | Name: Electrometer Consumption DS; Label: Consumption from DS; Value: 3
enum16 | CtType |  |  | Name: Gas Consumption; Label: Gas Consumption; Value: 4
enum16 | CtType |  |  | Name: Water Consumption; Label: Water Consumption; Value: 5
enum16 | CtType |  |  | Name: Inverter Production; Label: Production from Inverters; Value: 6
enum16 | CtType |  |  | Name: Tracker Production; Label: Production from Trackers; Value: 7
enum16 | CtType |  |  | Name: Battery Charge; Label: Energy stored into Battery; Value: 8
enum16 | CtType |  |  | Name: Battery Discharge; Label: Energy supplied from Battery; Value: 9
enum16 | CtType |  |  | Name: Meter Production; Label: Production from Meter; Value: 10
enum16 | CtType |  |  | Name: Meter Consumption; Label: Consumption from Meter; Value: 11
enum16 | CtType |  |  | Name: Meter Supply DS; Label: Supply to DS; Value: 12
enum16 | CtType |  |  | Name: Meter Consumption DS; Label: Consumption from DS; Value: 13
enum16 | CtType |  |  | Name: LUA Script Energy; Label: Energy computed by LUA Script; Value: 14
enum16 | CtType |  |  | Name: LUA Script Volume; Label: Volume computed by LUA Script; Value: 15
enum16 | CtUnit |  |  | Name: Wh; Label: Energy; Value: 0
enum16 | CtUnit |  |  | Name: m3; Label: Volume; Value: 1

## 64501
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Description | Notes
Header |  | 0 |  | 1 | ID | Counter Model | 64501 | uint16 |  |  | R | Include this model for Digital Input monitoring
Header |  | 1 |  | 1 | L |  | 1 + (Digital Input Count * 13) | uint16 |  |  | R | Model Length
Fixed Block |  | 2 | 0 | 1 | N | Digital Input Count |  | uint16 |  |  | R | Number of Digital Input Repeating blocks
Repeating Block |  | 3 | 0 | 1 | ID | Digital Input ID |  | uint16 |  |  | R | Digital Input ID
Repeating Block |  | 4 | 1 | 11 | Name | Digital Input Name |  | string |  |  | R | Digital Input Name from SM2 Digital Input Settings
Repeating Block |  | 16 | 1 | 1 | DIValue | Digital Input Value |  | enum16 |  |  | R | Digital Input Value (high/low)
enum16 | DIValue |  |  | Name: Input High; Label: High; Value: 1
enum16 | DIValue |  |  | Name: Input Low; Label: Low; Value: 0